## Room layout plan

| SBH Palette | POL pallet |
| --- | --- |
| Gebäudeschnitt | Building section |
| Hallenvorfeld | Apron |
| Verkehrs- und Rangierfläche | Traffic and manoeuvring area |
| Gabelstapler | Forklift |

Sample image:

## Structural and technical space requirements

| A | 1166 m² | POL storage building | 346 pallets in floor block storage |
| --- | --- | --- | --- |
| B | 150 m² | Apron |  |

The storage building for petroleum, oils, and lubricants (POL) is required for the value-retaining storage of hazardous substances in transportable containers.

Activities include storage and relocation, transport within the storage hall and, if necessary, disposal of released hazardous substances.

The height of the upper edge of the finished floor of the storage building is to be equal to the upper edge of the apron. To ensure that loads can be properly moved, sufficient manoeuvring and traffic areas must be available (3 m). The minimum corridor width is 2.5 m. The apron is to be constructed at a depth of 8 m over the entire width of the building. The storage building is to be protected from particularly strong heat sources.

It may be necessary to erect fire walls or additional storage areas to separate hazardous substances or to comply with permitted quantities of hazardous substances.

| Item | Quantity | Specifications | Remarks |
| --- | --- | --- | --- |
| Room temperature |  | 10 °C to 18 °C | A constant storage temperature in the specified spectrum is required. Store in a dry place and protected from heat sources. |
| Lighting A B |  | At least 200 lx At least 150 lx | LED lamps are to be installed where possible. The lighting is to be installed in such a way as to prevent the stored goods from heating up. B (150 lx) for the lighting of the loading area / apron |
| Power supply | - | - | - |
| Window(s) | - | - | No direct sunlight UV radiation |
| Door A | 2 2 | Double hinged door, steel Door, steel (emergency exit) | Width/height: 2 m / 2.5 m Width/height: 0.9 m / 2.1 m |
| Floor A B |  | Concrete floor | A: Anti-static, non-slip, oil-/acid-/alkaline-resistant, impermeable and non-absorbent Load-bearing capacity: ≥ 20 kN/m² To be trafficable with ground conveyors Weight of pallet: 500 kg B: Load category 1.0, road surface made of asphalt (IAW the Guidelines for the Standardisation of Pavement Structures for Traffic Areas 12/24). In order to prevent the ingress of surface water, appropriate drainage is to be planned for the gate area. |
| Walls/ceilings |  | Clear height: A ≥ 4,25 m | Smooth, light-coloured. Column-free if possible. |
| Ventilation |  | Maximum relative humidity 65 % Air-conditioning system (ventilation system) | Dry storage, ventilation system to prevent/reduce substance, moisture, gas and heat loads |
| Fire protection |  |  | Depending on the hazardous substances to be stored or their permitted net storage quantity, fire walls may be required. One fire detection and alarm system is to be installed per storage section. |

## Furnishings:

- Fire detection and fire alarm system