| German Army Headquarters Stationing/Infrastructure von-Hardenberg-Kaserne Prötzeler Chaussee 25 15344 Strausberg |  |
| --- | --- |

Statement of Requirements
(SOR ZAP 104)
Guard Building and 
Main Entrance Barracks

Long-term Infrastructure of the Bundeswehr as Part of 
Stationing a DEU Brigade in Lithuania

| Facility: | ZAPALSKIAI LTU |
| --- | --- |
| Location: Prepared by: | ZAPALSKIAI LTU DEU A HQ PAO Org Stationing/Infrastructure KdoHPAOOrgStatInfra@bundeswehr.org Tel. (Bw mil.): 90 - 8221 - 4453 Tel. (civ.): +49 (0) 3341 58 – 4453 |

Annexes:

- 4_1_04_01_space requirement_guard building

- 4_1_04_02_appendix_offices

- 4_1_04_03_appendix_server room

- 4_1_04_04_appendix_kitchen

- 4_1_04_05_appendix_cleaning items

- 4_1_04_06_appendix_clothing care

- 4_1_04_07_appendix_sanitary toilet

- 4_1_04_08_appendix_recreation room

#### Guard Building Infrastructure Requirements

# Infrastructure Requirements

## Guard building functional area

## General information / functional description / introductory note

The course of operations in the guard building requires a dedicated allocation of rooms.

- The duty room of the supervising guard [16 m²] constitutes the core area of the guard building. From this room, it must be possible to quickly alert the guard personnel in the recreation room for staff on duty [18 m²] and to issue weapons and ammunition at all times.

- Resting rooms [18 m²] are designed to allow short sleeping breaks of the guards for regeneration by day and night outside their duty and standby times. These rooms therefore require sound insulation and blackout blinds.

- The duty rooms (offices) of the supervising guard and the duty officer of the guard as well as the recreation room and the resting room will hence be equipped with an interior, lightproof, manually operated blackout system (e.g. break-proof roller blinds or curtains).

- An emergency exit is to be provided at the end of the corridor at the rear of the building as a rescue route in case of fire and for the rapid deployment of the guard in case of attacks and siege on the entrance side.

- The door of the emergency exit must open in the direction of escape away from the fence to the barracks.

- The door must be secured with a wide-angle spyhole and an unlocking alarm.

- Heating and cooling of the entire guard building is based on the relevant room and area logbooks and on the requirements as specified in the UKM LEAD SOR.

- The exterior shell of the building (especially exterior walls, access doors, windows) is to be a burglar-resistant RC 3 construction in accordance with DIN EN 1627. Windows up to 3 m above ground level must be fitted with attack-resistant P6B glazing in accordance with DIN EN 356 and with lockable security grade 2 window handles in accordance with DIN EN 13126-3.

- A wall lamp is to be installed at each corner of the building as part of installation defence lighting for illuminating the sides of the building and the surrounding area in case of danger.

- The pedestrian door at the main gate is to be equipped with a bell and an audio-visual intercom and opener system.

- A dedicated location for loading and unloading weapons – including a bullet trap – must be designated outside the guard building in its immediate vicinity.

- The size of the building connection rooms for the electrical, heating, water, and IT systems depends on the appliances and equipment to be installed. These rooms are accessible via external doors.

- The technical room for the intrusion detection system is exclusively accessible from the inside.

## Guard building room and space requirements

- Main entrance and forecourt of the building (controlled area):

- 2 m deep forecourt along the entire entrance side with a support-free canopy as protection against the weather

- Access door(s) to the guard building

  - Locking technology: resistance class 5 (high-protection, anti-drill) and grade 3 category of use in accordance with DIN EN 12209.

  - Burglar-resistant class ES 2 stainless steel plates as per DIN EN 18257.

  - When using tumbler locks: class H key identification requirements in accordance with DIN EN 12209.

  - When using cylinder locks: locking security class 6 and resistance class D locking cylinders as per DIN 18252 in conjunction with DIN EN 1303 or DIN EN 15684 respectively.

  - May only be opened from outside by personnel with authorisation for access.

  - The door(s) is/are to be technically monitored.

  - The main entrance door is to be additionally equipped with a wide-angle spyhole and a door bell to the office of the supervising guard or the SCC.

- Sufficient general lighting for the main entrance and the forecourt is to be ensured.

- Additional individually controllable lighting for illuminating the forecourt, the pedestrian gate and the waiting bays in front of the forecourt during personnel and vehicle checks must be available.

- Office of the duty officer of the guard [12 m²]

- Window providing an unobstructed view of the forecourt and the barracks area

- 1x telephone extension (fixed connection)

- other requirements see annex 3_1_04_02_appendix_offices

- Office of the supervising guard [16 m²]

- see annex 3_1_04_02_appendix_offices

- Vertically divided windows without grilles

- Draught-free transfer tray for identity checks in the centre window pane, with a stable working and writing surface on the outside. A maximum height of 1.0 m from the paved surface in front of the office to the upper edge of the transfer tray must be observed.

- The exterior wall including the windows, the transfer tray and the ID card pass-through must have penetration-resistant properties of resistance class FB 7 (NS) as per DIN EN 1522 or resistance class BR 7 (NS) as per DIN EN 1063.

- The room must be a burglar-resistant RC 3 construction in accordance with DIN EN 1627.  In this context, the following requirements for the door locking technology must be taken into account:

  - Resistance class 5 (high-protection, anti-drill) and grade 3 category of use as per DIN EN 12209.

  - Burglar-resistant class ES 2 stainless steel plate as per DIN EN 18257.

  - When using tumbler locks: class H key identification requirements in accordance with DIN EN 12209.

  - When using cylinder locks: locking security class 6 and resistance class D locking cylinders as per DIN 18252 in conjunction with DIN EN 1303 or DIN EN 15684 respectively.

  - Access from outside only for personnel with authorisation for access.

  - Opening of the door only upon entering a numeric identification code (e.g. PIN code). It must be possible to send out a duress alarm.

- Contractor-provided, permanently installed working surface (depth 0.5 to 0.6 m) with integrated communications technology along the entire window.

- Contractor-provided, clearly arranged operator panel integrated in the worktop with the following controls:

  - telephone extension (fixed connection),

  - stationary-battery telephone set as a co-station for the guard post alarm system,

  - buzzer of the bell system to the detention cells,

  - button for opening the pedestrian gate at the main entrance,

  - bell of the intercom system at the pedestrian gate,

  - communication station of the pedestrian gate intercom system,

  - additional siren alarm activation station (fire alarm only).

- 5x double socket 250 V/16 A; including one socket in the worktop and one socket for radio equipment in the exterior wall.

- Security Control Centre (SCC)

- The SCC room is used for operating, monitoring and controlling the surveillance system.

- The room must be a burglar-resistant RC 2 construction in accordance with DIN EN 1627. The door to the SCC must have a wide-angle spyhole. The door locking system must meet the following requirements:

  - Resistance class 5 (high-protection, anti-drill) and grade 3 category of use in accordance with DIN EN 12209.

  - Burglar-resistant class ES 2 stainless steel plate as per DIN EN 18257.

  - When using tumbler locks: class H key identification requirements in accordance with DIN EN 12209.

  - When using cylinder locks: locking security class 6 and resistance class D locking cylinders as per DIN 18252 in conjunction with DIN EN 1303 or DIN EN 15684 respectively.

  - Opening of the door only upon entering a numeric identification code (e.g. PIN code).

- SCC server room

- The SCC server room accommodates the premises’ security technology.

- The room is to be fitted with an intrusion detection system.

- The room must be a burglar-resistant RC 3 construction in accordance with DIN EN 1627. In this context, the following requirements for the door locking technology must be taken into account:

  - Resistance class 5 (high-protection, anti-drill) and grade 3 category of use in accordance with DIN EN 12209.

  - Burglar-resistant class ES 2 stainless steel plate as per DIN EN 18257.

  - When using tumbler locks: class H key identification requirements in accordance with DIN EN 12209.

  - When using cylinder locks: locking security class 6 and resistance class D locking cylinders as per DIN 18252 in conjunction with DIN EN 1303 or DIN EN 15684 respectively.

The room is to be constructed without windows. Other openings (e.g. for room ventilation or IT cooling) must be protected against sabotage (e.g. by full-surface flush mounts or by means of fine-meshed grilles). External split system air-conditioning devices or other cooling units for cooling sensitive IT/DP systems must be installed at locations that are inaccessible to unauthorised personnel or be structurally protected against unauthorised access, e.g. by means of enclosure or fencing.

- Recreation room for staff on duty

- see annex 3_1_04_10_appendix_recreation room incl. fitted kitchen [4 m²]

- The locks/locking technology of the door to the recreation room for staff on duty must meet the following requirements:

  - Resistance class 5 (high-protection, anti-drill) and grade 3 category of use in accordance with DIN EN 12209.

  - Burglar-resistant class ES 2 stainless steel plate as per DIN EN 18257.

  - When using tumbler locks: class H key identification requirements in accordance with DIN EN 12209.

  - When using cylinder locks: locking security class 6 and resistance class D locking cylinders as per DIN 18252 in conjunction with DIN EN 1303 or DIN EN 15684 respectively.

- Resting rooms for guard personnel [18 m²]

- Sound-insulated window and door

- Window with a fixed lower field and an upper field designed as bottom-hinged sash

- 2x double socket 250 V/16 A

#### Main Entrance Barracks Infrastructure Requirements

- Infrastructure Requirements

  - Main entrance functional area

    - General information / functional description / introductory note

Example image 1 – entry and exit area (sketch)

| Kasernenzaun | Installation perimeter fence |
| --- | --- |
| Flaggenmasten | Flagpoles |
| 8 Besucherparkplätze | 8x visitor parking space |
| Schiebbares oder schwenkbares Rolltor | Sliding or swivelling roller door |
| Standstreifen Pkw | Passenger car bay |
| Ausfahrt | Exit |
| Einfahrt | Entrance |
| Standstreifen Lkw | Truck bay |
| Fußgängertor | Pedestrian gate |
| Wachgebäude | Guard building |

- Location

- Main entrance and exit, only in conjunction with guard area and preferably near the headquarters area

- Emergency exit, generally in a sector at the opposite end of the compound

- Secondary entrances and exits, preferably near the storage area, the technical support/maintenance area or the vehicle parking area

The main entrance and exit complex consists of the following elements:

- Main entry and exit gate

- Pedestrian gate

- Barrier system

- Driving lanes

- Stopping strips/bays

- Visitor parking bays

- Flagpoles

- Lighting

- Main entry and exit gate

At the main entrance/exit, a sliding or swivelling steel lattice gate with supporting rollers and a vertical serrated metal strip on the upper chord is required.

- Height: 2 m

- Width: 4.25 m

The gates must cover the entire area of the roadway and be visible from the guard building.

- Pedestrian gate

A pedestrian gate (steel lattice gate with a vertical serrated metal strip on the upper chord) is required on the pedestrian sidewalk to the right of the entrance:

- Height: 2 m

- Width: 1 m

The gate must be visible from the guard building and is to be fitted with an intercom system, a bell button and an electric door opener.

- Barrier system

Electrically operated barriers are to be installed in offset arrangement behind the entry gate and in front of the exit gate on a traffic island at the level of the room of the guards on duty. In case of a power failure, they must be operable manually.

A sentry box with three single-glazed viewing windows is to be installed on the traffic island as a shelter for the gate guard.

- Driving lanes

One lane each is required for the incoming and the outgoing traffic with vertical sloping curbs, a width of 4 m and a traffic island in between the lanes.

Example image 2 – traffic island with sentry box

| Postenhaus | Sentry box |
| --- | --- |

- Stopping strips

In order to ensure a smooth traffic flow in the area of the main entrance, stopping strips are to be laid out inside and in front of the premises, which can be used as short-term waiting bays in case of need.

The following requirements must be met: (Example image 1)

|  | Exit | Entrance |
| --- | --- | --- |
| Within the premises | 1x stopping strip 2.30 m x 10 m for passenger cars just before the exit | 1x stopping strip 2.30 m x 10 m for passenger cars between entry gate and barrier |
|  |  | 1x stopping strip 3 m x 25 m for trucks behind the barrier |
| Outside the premises |  | 1x stopping strip 3 m x 25 m for trucks outside the gate |

- Visitor parking

For visitors to the barracks, additional provisions are to be made for eight (8) parking bays outside the premises and six (6) parking bays inside the premises in the immediate vicinity of the guard building. (Example image 1)

- Lighting

The lighting of the main entrance area is to be connected to the road lighting of the facility. It is to be controlled automatically via a daylight control but must also be switchable manually by the guards. Lampposts are to be installed at a distance of at least 1 m from the kerb.

- Nominal illuminance (En): 100 lx (vehicle and identification checks)

- Emergency exit

The stated requirement is a sliding or swivelling steel lattice gate with supporting rollers and a vertical serrated metal strip on the upper chord:

- Height: 2 m

- Width: 5.25 m

- Lighting as at the main gate

- Secondary entrance and exit

The stated requirement is a sliding or swivelling steel lattice gate with supporting rollers and a vertical serrated metal strip on the upper chord:

- Height: 2 m

- Width of the access and exit road: 8.50 m

- Connection to the main thoroughfare of the premises

- Electrical/mechanical barrier system

- Sentry box, a small guardhouse with a paved forecourt

- Lighting as at the main gate

Example image 3

| Postenhaus | Sentry box |
| --- | --- |
| (Prinzipskizze ohne Maßstab) | (simplified sketch, not to scale) |

- Sentry box at secondary entrances

The sentry box (example image 3) is to be installed on the right side of the entrance.

- Paved forecourt between the building and the footpath with

  - an outdoor luminaire to illuminate the forecourt, the footpath, the barriers and the entrance

- Hexagonal precast construction (floor area of 8 m²) with

  - a side length of approx. 1.75 m.

  - one side parallel to the road and footpath

  - a fixed window

  - interior blackout blinds (no curtains)

  - 1x double socket 250 V/16 A

  - 1x telephone extension (fixed connection)

  - heating: as stated in the requirements for the guard building

  - The exterior wall including the window must have penetration-resistant properties of resistance class FB 7 (NS) as per DIN EN 1522 or resistance class BR 7 (NS) as per DIN EN 1063.