The servers required for operation will be set up and administered in this room. Room layout plan

Sample image:

| Funktionsfläche | Functional space |
| --- | --- |
| Doppelsteckdose 250V/WS/16A | Double socket 250 V/AC/16 A |
| Netzwerkanschluss Cat 6 Datendoppeldosen | Double data socket for Cat-6 network connection |

## Structural and technical space requirements

| Item | Quantity | Specifications | Remarks |
| --- | --- | --- | --- |
| Room temperature |  | 10°C – 35°C | Air conditioning by means of a climate-control system is to be provided |
| Lighting |  | At least 500 lx | LED lamps are to be installed where possible. |
| Power supply in rooms | 4 | Double socket 250 V/AC/16 A | A system ensuring uninterrupted power supply is to be provided. |
| IT connection | 4 | Cat-6 double data sockets | Network connection |
| Window(s) |  | Windows with RC-2 attack-resistant P5A glazing in accordance with DIN EN 356 |  |
| Door | 1 | Intrusion-resistant design (RC 2 in accordance with DIN EN 1627, door with locking technology) | Width/height: 985 mm / 1985 mm |
| Floor |  | Linoleum | Level and easy to clean |
| Walls/ceilings |  | Room height: 3.00 m | Flat, smooth, light-coloured Suspended ceilings to allow routing of cables |
| Ventilation |  | Relative humidity: ≤ 80%; absolute humidity: ≤ 20g/m³ | Dehumidifier, if necessary |