## Room layout plan (example)

- Toilet rooms are facilities where persons can wash themselves or use the toilet or urinal.

Circulation route

Washing stations

Toilet cubicle

Movement area

Toilet anteroom

## Structural and technical space requirements

- The toilet rooms comprise at least one toilet and one hand wash basin; and, if required, a urinal and a toilet cubicle.

- The toilet rooms must be located in the vicinity of workplaces, break rooms, ready rooms, washrooms or locker rooms.

  - The path to toilet rooms should not exceed 50 m and must not exceed 100 m.

  - Therefore, the toilet rooms should be distributed within a work facility in such a way that they are not more than 100 m away from permanent workplaces.

- The toilet cubicles are spaces that can be locked from the inside, are separated from the toilet room by partition walls, and incorporate a toilet.

- A toilet anteroom is a completely separate area within a toilet room so as to prevent, for example, smelly air from transpiring into other areas and, possibly, to accommodate the hand wash basins.

- Sports hall (large): 3x large unit and 2x small unit

Large unit: one toilet (toilet bowl) and one hand wash basin

Small unit: one toilet (toilet bowl)

Sports hall area: for female service personnel:
one toilet (bowl) and hand wash basin

Sports hall area: for male service personnel:
one urinal, one toilet (bowl) and hand wash basin

In addition: A barrier-free individual changing room with a lounger (6.0 m²) with direct access to the separate room with a toilet (gender-neutral), shower, folding seat and hand wash basin.

- Separate sanitary facilities must be established for male and female service personnel.

- Servicewomen are to be taken into consideration with a percentage of 15% (or 50% in the Bundeswehr Medical Service) when planning common sanitary facilities.

- For sanitary facilities that are to be used by all genders, no urinals are to be required.

- The number of toilets and urinals is determined using Tables 1 and 3.

  - Simultaneous use is the decisive factor in determining the required sanitary facilities.

  - High level of simultaneous use 
(e.g. classroom building).

  - For male personnel, from the toilets and urinals to be provided, at least one third is to be toilets, the rest urinals.

| Maximum number of persons who normally use the toilet rooms | Toilets/urinals | Hand wash basins |
| --- | --- | --- |
| Up to 5 | 2 | 1 |
| 6 to 10 | 3 | 1 |
| 11 to 25 | 4 | 2 |
| 26 to 50 | 6 | 2 |
| 51 to 75 | 7 | 3 |
| 76 to 100 | 9 | 3 |
| For each additional 30 | +2 | - |
| For every additional 60 | - | +1 |

Table 1

  - Room layout plan for 33x personnel

Toilet room: (33x personnel / 100%) * 15% = 5x servicewomen

Table 1: 2x toilet, 1x hand wash basin

Circulation route

Washing station movement area
0.5 m2

Toilet cubicle movement area
0.5 m2

Toilet cubicle

Toilet anteroom

Washing station

Toilet room: 33x personnel – 5x servicewomen = 28x servicemen

Table 1: 6x toilet/urinal, 2x hand wash basin

One-third rule: 6x * 1/3 = 2x toilet, 4x urinal, 2x hand wash basin

Circulation route

Urinal movement area
0.36 m2

Urinal

  - Low level of simultaneous use.

  - For male personnel, of the toilets and urinals to be provided, at least one third is to be toilets, the rest urinals.

| Maximum number of persons who normally use the toilet rooms | Toilets/urinals | Hand wash basins |
| --- | --- | --- |
| Up to 25 | 2 | 1 |
| 26 to 50 | 3 | 1 |
| 51 to 75 | 5 | 2 |
| 76 to 100 | 6 | 2 |
| For each additional 30 | +1 | - |
| For every additional 60 | - | +1 |

Table 3

  - Room layout plan for 36x personnel

Toilet room: (36x personnel / 100%) * 15% = 6x servicewomen

Table 1: 2x toilet, 1x hand wash basin

Circulation route

Washing station

Washing station movement area
0.5 m2

Toilet cubicle movement area
0.5 m2

Toilet cubicle

Toilet room: 36x personnel – 6x servicewomen = 30x servicemen

Table 1: 3x toilet/urinal, 1x hand wash basin

One-third rule: 3x * 1/3 = 1x toilet, 2x urinal, 1x hand wash basin

Circulation route

Urinal movement area
0.36 m2

Urinal

| Item | Quantity | Specifications | Remarks |
| --- | --- | --- | --- |
| Room height |  | Minimum vertical clearance of 2.50 m |  |
| Toilet cubicles |  | Partitions, doors that do not go up to the ceiling must have a minimum height of 1.90 m | Are spaces that can be locked from the inside, are separated from the toilet room by partition walls, and incorporate a toilet. |
| Toilet anteroom |  | There must not be any urinals in the anteroom. | Is a completely separated area to accommodate possible hand wash facilities. |
| Mechanical ventilation |  | Ventilation system | Must be designed in such a way that an exhaust air volume flow of 11 m³/(h m²) is achieved. The exhaust air from toilet rooms must be prevented from entering other rooms. |
| Natural ventilation (window ventilation) |  | Minimum cross section single-sided ventilation: 0.17 m2 / toilet 0.10 m2 /urinal *cross ventilation: 0.10 m2 / toilet 0.06 m2 / urinal | The values provided are the sum of the supply and exhaust air area. *Air vents in opposite external walls or in an external wall and the ceiling surface. |
| Partition walls, doors, windows |  | Must be arranged/constructed in a way that prevents persons on the outside from looking in | The ventilation of sanitary facilities must be designed in a way that prevents draughts when in use. |
| Floors |  | Must be designed in such a way that moisture cannot penetrate or rise from the ground. | Must be easy to clean. Must be slip-resistant even when wet. |
| Walls |  |  | Must be easy to clean. |
| Lighting |  | Minimum value: Intensity of illumination (E): 200 lx Minimum value: Colour rendering index Ra: 80 | If mirror lighting is used, the minimum level of vertical illumination intensity must be 500 Ix. |
| Marking |  | Sign on the door | Sanitary facilities must be clearly indicated. |
| Air temperature |  | +21oC | Due to user-initiated ventilation processes, the air temperature in toilet rooms may fall below the minimum for a short period of time. |
| Heating |  |  | Heating systems must be arranged, designed or shielded in such a way that personnel are protected from incidental contact with surfaces that are too hot. |
| Noise protection |  |  | No special requirements |

## Furnishings:

| Item | Quantity | Remarks |
| --- | --- | --- |
| Each toilet room |  | If containing only one toilet, toilet rooms with a door to the hallway must be lockable from the inside. Additionally, they must be equipped with a clothes hook, toilet paper holder, waste container and toilet brush. |
| Each toilet cubicle |  | One toilet only, must be lockable from the inside. Additionally, they must be equipped with a clothes hook, paper holder and toilet brush. In every toilet used by females, a hygienic waste bin with cover is to be provided. |
| Toilet anteroom |  | Hand wash basin with working cold-water connection, mirror, shelf and lighting (on the side of or above the mirror). |
| Hand wash basin |  | + 1x liquid soap dispenser + 1x paper towel dispenser with waste container (for used paper towels), |