Table of contents

1	Preliminary remarks on illustrations	1

2	Structural and technical space requirements	1

2.1	General information	1

2.2	Laying of cables	3

2.3	Routes and cable-laying systems	11

2.4	Special requirements for low-voltage power supply	12

2.5	Special requirements for IT lines	16

2.6	Special requirements for communications cables / telephone lines	30

2.7	Special requirements for distribution cabinets / racks	31

2.8	Special requirements for other networks	37

# Preliminary remarks on illustrations

- Illustrations from the Handbuch IT-Leitungsnetze (IT networks manual) are included wherever deemed useful for explanatory purposes.

# Structural and technical space requirements

## General information

- The Bundeswehr facilities in Lithuania are facility category 1 and service class 1 facilities.
Facilities of facility category 1 are provided with a redundant WAN connection to two separate central distribution boards.

Figure 1: Facility class 1

| Serviceklasse SK-1 | Service class SK-1 |
| --- | --- |
| Gebäude – EV | Building - floor distributor |
| GV | Building distributor |
| GV-EV | Building / floor distributor |
| Liegenschaftsverteiler | Central distribution board of the facility |
| Core | Core |
| WAN CE 1 (LZK) | WAN CE 1 (facility access node) |
| WAN PE | WAN PE |
| Mindestens getrennte Brandabschnitte | At least separate fire-protection areas |
| Getrennte Hauseinführung (mind. 1m Abstand zwischen 1 und 2) | Separate building inlets (with a distance of at least 1 m between 1 and 2) |
| Nicht getrennte Hauseinführung, Nutzung gleicher Kabel; Unterschiedliche Kabel | Building inlet not separated, use of the same cables, different fibres |
| Nicht getrennte Hauseinführung, separate Kabel, getrennte Trassenführung der Kabel | Building inlet not separated, separate cables, separate cable routes |
| Layer3 link | Layer3 link |
| Layer2 link | Layer2 link |

- The requirements specified in this document are adapted from the internal Bundeswehr networks guideline.

- They assume the facilities are provided with a fully wired network.

- For Bundeswehr IT networks, the following standards apply:

  - Ethernet (IEEE 802.3)

  - Wireless LAN (IEEE 802.11)

- xDSL - Technologies for connections in the primary region via existing copper cables (on hand / in justified exceptional cases)

- As a matter of principle, all installed components and cable systems must be documented and labelled.

- Any cables and lines that have been laid must be labelled unambiguously so that wiring errors or mixing up of cables/wires can be avoided as early as during installation. Labelling with line numbers is done according to the cable laying plans of the implementation project.

- Each distribution cabinet / rack frame must be labelled accordingly. Durable labels must be attached to the front side of the distribution cabinets / rack frames so that they are clearly visible from the outside.

- After the installation of the cables and connections has been completed, all end points of a cable path on the splice boxes, distributor panels, LSA-PLUS modules and connecting boxes must be labelled.

- The Handbuch IT-Leitungsnetze (IT networks manual) is based on the standards series DIN EN 50173, 50174, 50310 and 50346.

## Laying of cables

- Underground cable routes must be laid as directly as possible, taking account of the permissible bending radii of the cables.

- Redundant cables (e.g. in facility category 1 facilities) must be laid with a minimum distance of 2 m from each other.

- If possible, roads and trails are to be crossed at right angles, using cable conduits or conduit bricks. In doing so, additional reserve conduits must be laid. Occupied and unoccupied cable drafts must be sealed on both sides by means of sealing caps or blank plugs in order to prevent dust and small animals from getting inside.

- Cables and joints must be installed in a way that the assembly work can be executed, the cable ditches are not wider than necessary and future operation and maintenance work can be conducted without difficulties.

- Installation instructions for twisted pair (TP) cables (IAW DIN EN 50174-2)

  - Before the installation, all cable drums must be measured. This measurement serves, on the one hand, to determine the delay factor and, on the other hand, to check the cable.

  - Cables must always be protected against humidity. They may already be damaged by incorrect handling of the cable drum or improper storage.

  - The installation of cables must be checked with due care within the framework of construction management.

  - • Cables must never - not even during the installation - be kinked.

  - • Minimum bending radii and maximum tensile forces are cable-specific data. As a rule, a minimum bending radius of at least 8 times the cable diameter must be observed, this corresponds to approximately 6 cm.

  - • Cables must never be squeezed.

  - • If cables are installed in cable harnesses and operated via remote supply (PoE), the rise in temperature in relation to the current-carrying capacity must be considered. Cable harnesses must be installed with an appropriate spacing. In new systems, cable harnesses should not comprise more than 24 individual cables (DIN EN 50174-2, Supplement 1).

- Installation instructions for fibre-optic cables

  - Internal fibre-optic cables must always be protected against humidity. The ends of external fibre-optic cables must be sealed in a watertight manner during storage and transport.

  - If fibre-optic cables are drawn in mechanically, measurement protocols must be recorded in order to ensure that the maximum tensile forces were not exceeded. Before drawing in the cable, the angles in shafts and buildings must be equipped with cable runs or rollers so that the minimum bending radii of the cables are observed.

  - External cables should not be drawn in at temperatures below 0°C. In addition, the installation instructions of the manufacturer must be observed.

  - As far as fire classifications are concerned, EU Directive 305/2011 is to be observed.

- The cables must be positioned symmetrically to the axis of the cable route. If several cables must be laid simultaneously, they must be arranged side by side on the ditch bottom. Care must be taken to ensure that the cables are not crossed (danger of confusion during future operating works).

- All external cables must be water-protected in longitudinal and transversal direction and provided with a non-metallic rodent protection if they are not installed inside a protective pipe. An appropriate external cable is included in the following table.

Figure 2: Guide values for external cables in accordance with DIN EN 60794-3

| Außenkabel | External cables |
| --- | --- |
| Kabelaufbau und Kennzeichnung gemäß DIN EN 60794-1-1, Beiblatt 1 | Cable design and marking IAW DIN EN 60794-1-1, Supplement 1 |
| Außenmantel flammhemmend, eventuell halogenfrei | Outer sheath fire-retardant, possibly halogen-free |
| Metallfreier Nagetierschutz und Zugentlastung kombiniert | Non-metallic rodent protection and strain relief combined |
| Zentrales Zug- und Stützelement (nichtmetallisch) | Central strain and support element (non-metallic) |
| Weitere Eigenschaften, wie z.B. | Further features such as |
| Temperaturbereich (fest verlegt) | Temperature range (firmly mounted) |
| Wasserdichtigkeit (längs / quer) | Waterproofness (lengthwise / crosswise) |
| UV-Resistenz | UV resistance |
| Mechanische Beständigkeit | Mechanical resistance |
| Minimale Biegeradien | Minimum bending radii |
| Multimode-Fasern | Multi-mode fibres |
| Bandbreite-Längenprodukt | Bandwidth distance product |
| Dämpfung | Loss |
| Min. Linklänge (1 Gbit/s – Ethernet) | Minimum link length (1 Gbit/s – Ethernet) |
| Numerische Apertur | Numerical aperture |
| bei | at |
| nm | nm |
| Ps/(nm*km) | Ps/(nm*km) |
| dB/km | dB/km |
| Singlemode-Fasern | Single mode fibres |
| Chromatische Dispersion | Chromatic dispersion |
| Dämpfung | Loss |
| Nom. Nulldispersionswellenlänge | Nominal zero dispersion wavelength |
| Kabelgrenzwellenlänge | Cable cut-off wavelength |
| Polarisationsmoden | Polarisation modes |
| Dispersionskoeffizient (PMD) | Dispersion coefficient (PMD) |

- All unarmoured communications cables and all fibre-optic cables can be installed in cable duct systems consisting of plastic pipes or concrete conduit bricks.

- In the Bundeswehr, the minimum cover for underground cables and cable ducts is 0.8 m. If cable duct systems are provided with two pipes for the connection of individual buildings, it may in certain cases (low risk of danger to the cable route due to the local conditions) be possible to use a reduced ditch profile with a cover of 0.5 m.

Figure 3: Route profiles

| Ggf. befestigte Oberfläche | If required, paved surface |
| --- | --- |
| Trassenwarnband | Route warning tape |
| Wieder eingebrachter Aushub | Backfill |
| Füllsand | Backing sand |
| Standardprofil | Standard profile |
| Reduziertes Profil | Reduced profile |

- In any case, a continuous cable route tape must be installed approx. 0.30 m above the upper edge of the cable. If more than 3 communications cables are positioned in the same ditch, 2 route tapes must be positioned above the two outer cables.

- Cable duct systems must be built for cable routes the existence of which is secured for the long term. Cable duct systems have the following significant advantages:

  - The cable routes will be secured for cables to be laid at a later date.

  - The access to the cables - particularly to splice joints - will be unrestricted, and troubleshooting measures can be conducted rapidly.

  - Cables no longer required can be pulled out at low cost, and single-pair cables can be replaced by multi-pair cables.

- Fibre-optic cables must always be installed in cable duct systems.

- Cable duct systems must be built by using cable protective pipes. A multi-duct pipe may be installed in order to better exploit a cable duct. Normally, a multi-duct pipe consists of four pipes, two pipes with an inside diameter of 28 mm, two pipes with an inside diameter of 35 mm. Cables with an outside diameter ≤  18 mm can be installed in the small pipes, cables with an outside diameter ≤ 25 mm in the large pipes.

- Cable shafts and junction boxes must be dimensioned as follows:

  - Provide an adequate size to offer sufficient space for additional cables and cable fittings which may be required for the future final configuration as well as for laying and installation activities and to enable cables with a greater bending radius to be installed.

  - Provide an active drainage if required

  - Avoid switching points in the cable shaft because of the existing humidity (switching points in junction boxes are not permitted).

- Micro-Cable System (MCS), multi-pipe system for the direct laying of fibres

  - If a cable duct system is planned to be built exclusively for the installation of a primary network consisting of fibre-optic cables, in exceptional cases it is possible to use multi-pipe systems as an economical alternative to conventional cable duct systems. These systems, which are also used by carriers for the direct fibre-optic supply to buildings (Fibre to the home - FTTH), have been tried and tested.

- Introduction of cables into buildings

- If cables are introduced into buildings, the minimum distance between the cable and power cables and other systems (water pipes etc.) must be at least 0.50 m. State-of-the-art combined inlets with smaller distances are permitted. Only components which ensure a permanent gastight, watertight and, if required, pressure-resistant sealing may be used for the introduction of cables.

- External fibre-optic cables will be connected to fibre-optic cable termination frames or fibre-optic cable termination holders. If the fibre-optic cable termination frame/fibre-optic cable termination holder is not located in the same fire area as the cable inlet, the transition joints must be installed in the room with the cable inlet, and internal fibre-optic cables must be installed to connect the fibre-optic cable termination frame/fibre-optic cable termination holder.

- Internal fibre-optic cables must be used as connecting cables with the fibre-optic cable termination frame/fibre-optic cable termination holder.

- Splice cassettes will be used for splicing the fibres at the fibre-optic cable termination frames / fibre-optic cable termination holders.

- Unused ports / through-type couplings on fibre-optic cable patch panels must be protected by protective caps against environmental influences like dust.

- All cables must always be terminated by ending devices. They must enable opening and measuring of the lines.

- Cable ending devices outside buildings may comprise the following:

  - Junction boxes (60), (62), 70 with overvoltage protection

  - Cable distribution boxes

  - Terminal distribution boxes

- As cable ending devices in buildings,

  - terminal boxes

  - disconnecting links

  - terminal strips

  - weatherproof wall-mounted distributors for 40 twin wires with change-over switch for 10 twin wires

  - terminal distribution boxes suitable for outdoor and indoor use

may be used, which may be installed in

  - cable termination racks

  - wall-mounting distribution boards

  - floor-mounted distribution boards

  - cable cabinets

  - cable distribution boxes, and

  - terminal housings

may be installed.

- The following devices may be used as terminal boxes, disconnecting links and terminal strips:

  - Disconnecting terminal blocks with U-link connectors

  - Disconnecting terminal blocks with clamping devices for cables to be casted

  - Solderless, screwless and stripless quick-connect designs (terminal strips, disconnecting links, earth modules)

  - Disconnecting link 62 for 40 twin wires (only for extensions)

  - Disconnecting link 55 for 25 twin wires (only for extensions)

  - Disconnecting link for 10 twin wires

- On principle, soldering technologies must no longer be used.

## Routes and cable-laying systems

- Each multi-storey building or building with a basement will be provided with one or several vertical cabling pathways leading to the floor distributors. The floor distributors will supply the workplaces and IT rooms.

- The cable risers should preferably be installed near the central distribution rooms.

- The unshielded cables for the IT power supply and the shielded IT lines will run in a tray or in parapet ducts

  - between floors in cable risers which are usually fitted with a separator, or separate cable risers for electric power, data and measurement/control cables will be installed;

  - on the individual floors in metal electrical installation duct systems which are designed to ensure the separation of the power lines from the data and measurement/control lines.

- Metal routing systems and their accessories must be included in the measures against electric shock.

- Cable routing within corridors, staircases or escape ways must be avoided. If necessary, fire protection ducts must be used.

- In case of comprehensive internal networks, cable shafts must be provided as risers. Riser shafts are to run from the basement to the top floor without lateral offset. They may become narrower towards the top. Their width depends on the number of cables to be laid and the number of floors.

- Joint cable shafts may be used for IT cables and power cables.

- The installation cables must be laid orderly in brackets, on cable racks, etc. No distributors are to be installed in suspended ceilings.

- As regards raised floors, installation cables must be laid orderly on the subfloor.

- Rigid or flexible conduits made of metal or plastic can be used for electrical installation systems. They must be selected with due regard to the local conditions and the given material stress.

- The conduit networks for communication lines must be arranged in such a way that no water can penetrate them and no condensation water can accumulate there. They must be routed vertically or horizontally. The conduits must be laid so that the lines cannot be damaged when drawing them in. They must therefore be fitted with a protection at their free ends (e.g. grommets).

- Surface-mounting is required where conduit networks or other concealed routings cannot be established or are economically unjustifiable, e.g. in basement rooms, protective shelters, attics, garages and workshops.

## Special requirements for low-voltage power supply

- Starting at the main distributor of the building, the power supply network of IT equipment must be provided as a TN-S system.

- Up to four rooms with a maximum of 12 sockets are to be connected to one electric circuit. Sockets for IT equipment must be provided with special labels.

- A combined two-pole (1P+N) residual current device (RCD) with a miniature circuit breaker (also called “residual current circuit breaker with overcurrent protection” – RCBO) must be provided for each circuit in the sub-distribution.

- Equipotential bonding: In order to rule out uncontrolled flashovers in the building installation in case of a lightning stroke and to prevent dangerous shock currents, metal structures, electrical systems, lightning protection systems and earthing systems will be directly connected with lines at the main earthing bar. The main earthing bar will be installed in the basement or on the ground floor, e.g. next to the main low-voltage distribution frame. The main earthing bar must be designed and installed in such a way that it is easily accessible for inspection purposes.

Figure 4: Example of an earthing system with protective equipotential bonding

| IT-Schrank | IT cabinet |
| --- | --- |
| IT-Verteilerraum | IT distribution room |
| LWL-Patchfeld-P1 | Fibre optic patch panel P1 |
| Geräteanschluss | Device connection |
| Gerät (Switch-1) | Device (switch 1) |
| Gerät (Switch-n) | Device (switch n) |
| Patchfeld-P2 | Patch panel P2 |
| Patchfeld Pn | Patch panel Pn |
| 2 x Cu-Potenzialausgleichsschiene | 2x copper equipotential bonding bar |
| Schrankanschluss | Cabinet connection |
| Potenzialausgleichsschiene IT-Raum | IT room equipotential bonding bar |
| Gestellpotenzialausgleichsleiter nach DIN EN 50310 | Rack equipotential bonding conductor IAW DIN EN 50310 |
| Optionale Verbindung (nur bei notwendiger Vermaschung) | Optional connection (only if intermeshing is required) |
| Örtliche Potenzialausgleich (Etagenpotenzialausgleich) | Local equipotential bonding (floor equipotential bonding) |
| Potenzialausgleich BR-Kanal und weitere metallische Teile | Equipotential bonding of parapet duct and other metal elements |
| Schutzpotenzialausgleichsleiter nach DIN VDE 0100-540 | Protective equipotential bonding conductors IAW DIN VDE 0100-540 |
| Potenzialausgleichsleiter ≥25 mm² nach DIN EN 50310 | Equipotential bonding conductor ≥25 mm² IAW DIN EN 50310 |
| Haupterdungsschiene | Main earthing bar |
| Fundamenterder | Foundation earth electrode |

- In facility category 1 and 2 facilities, the low voltage distributions in the central distribution boards of the facility are to be operated with emergency power systems. The same applies to the distributions in building and floor distributors of facility category 1 buildings.

- Emergency power systems and load shedding of general power supply circuits must be configured to guarantee uninterrupted operation of the IT network and of telecommunications.

Figure 5: Emergency power system principle for standby supply

| UV-AV | General power supply sub-distributor |
| --- | --- |
| UV-NEA | Emergency power system sub-distributor |
| NSHV-AV | Main low-voltage distribution frame - general power supply |
| Kuppelschalter AV-NEA (optional) | General / emergency power supply bus-type breaker (optional) |
| NSHV-NEA | Main low-voltage distribution frame - emergency power system |
| HV-NEA | Emergency power system main distribution frame |
| NEA | Emergency power system |
| Netzersatzanlage NEA stationär Gebäude oder Container | Static emergency power system, building or container |
| Anschlusskasten für NOT-Einspeisung | Junction box for EMERGENCY power supply |
| Netzersatzanlage NEA mobil (Wartung, etc.) | Mobile emergency power system (maintenance etc.) |

## Special requirements for IT lines

- In the primary and secondary regions, fibre optic technology is standard: (xDSL via existing copper communication lines are only permitted in justified exceptional cases)

- In general, cables with single-mode fibres (at least category OS2) are used for the primary IT network. For “other networks” multi-mode fibres (at least category OM4) may be used, if required. In that case, a separate fibre optic cable is to be laid.

- When dimensioning the fibre-optic cable connections between the building distributors and within the buildings of a facility, four fibre-optic cables must be provided for the building automation systems if the cables are routed in parallel. If the building automation requires multi-mode fibres, an additional cable is to be included. The distributors must be provided with separate connections for the building automation systems.

- In the tertiary region, copper cables of category 7, Screened Foil Twisted Pair (S/FTP) cables or rather cables which support 10GbE are used [if there are particular demands on bandwidth / transmission rate, fibre-optic cables are used as well (FTTO / FTTD)].

- RJ45 connector components of link class EA, which also support 10GbE are used as links.

Figure 6: RJ45 pair assignment in accordance with DIN EN 50173-1

| Paar | Pair |
| --- | --- |
| Stiftanordnung | Pin configuration |

Figure 7: RJ45 pin assignment

| Pin | Pin |
| --- | --- |
| S | S |
| E | E |
| W | W |
| a | a |
| b | b |
| TX | TX |
| RX | RX |
| D | D |
| X | X |
| Telefon analog (Int. Norm) | Analog telephone (international standard) |
| Telefon analog (Siemens) | Analog telephone (Siemens) |
| Telefon analog (DTAG) | Analog telephone (DTAG) |
| DSL-Splitter | DSL splitter |
| ISDN (UK0/UP0) | ISDN (UK0/UP0) |
| Ethernet 10/100BaseT | Ethernet 10/100BaseT |
| Gigabit-Ethernet | Gigabit-Ethernet |
| Token Ring | Token Ring |
| TP-PMD | TP-PMD |
| IBM AS 400 | IBM AS 400 |
| IBM 3270 | IBM 3270 |
| ATM | ATM |
| Legende | Legend |
| A = A-Ader (1a = A-Ader 1 / 2a = A-Ader 2) | A = A-wire (1a = A-wire 1 / 2a = A-wire 2) |
| B = B-Ader (1b = B-Ader 1 / 2b = B-Ader 2) | B = B-wire (1b = B-wire 1 / 2b = B-wire 2) |
| E = Erde | E = earth |
| W = Wecker | W = bell |
| RD = Received Data (Empfangsdaten) | RD = received data |
| TD = Transmitted Data (Sendedaten) | TD = transmitted data |
| S = Shield (Abschirmung) | S = shield |
| Quelle: www.elektronik-kompendium.de (Jan 2017) | Source: www.elektronik-kompendium.de (January 2017) |

Figure 8: TIA 568, contacts and colours

| Kontakt | Contact |
| --- | --- |
| Paar-Nr. nach TIA | Pair no. according to TIA |
| Farbe | Colour |
| Weiß/grüner Strich | White / green |
| Grün/weißer Strich | Green / white |
| Weiß/oranger Strich | White / orange |
| Blau/weißer Strich | Blue / white |
| Weiß/blauer Strich | White / blue |
| Orange/weißer Strich | Orange / white |
| Weiß/brauner Strich | White / brown |
| Braun/weißer Strich | Brown / white |

- Only connecting boxes with fully screened individual RJ45 modules (e.g. Keystone) with a certification for Class EA transmission systems may be used. Modules with dust covers are to be used.

- In order to improve the protection of the patch cables, the connecting boxes must permit a module arrangement with a slanted outlet. Slanted outlet means that the RJ45 sockets are be inclined downward so that the patch cables are better protected against damage.

- In the primary region, there will be a redundant WAN connection to two separate central distribution boards of the facility.

- In the primary and secondary regions, layer-2 and layer-3 switches are used and a transmission speed of up to 10 Gbit/s will be provided.

- Route lengths of external fibre optic networks:

Figure 9: Longest supported physical connection with multi-mode optical fibres

| Netzanwendung (Übertragungsrate) | Network application (transmission rate) |
| --- | --- |
| Wellenlänge | Wavelength |
| Streckendämpfung | Loss per line |
| Multimode-Fasern | Multi-mode fibres |
| OM | OM |
| BASE-FL | BASE-FL |
| BASE-FX | BASE-FX |
| BASE-SX | BASE-SX |
| BASE-LX | BASE-LX |
| BASE-SR/SW | BASE-SR/SW |

Figure 10: Longest supported physical connection with single-mode optical fibres

| Netzanwendung (Übertragungsrate) | Network application (transmission rate) |
| --- | --- |
| Wellenlänge | Wavelength |
| Maximale Streckendämpfung | Maximum loss per line |
| Singlemode-Fasern | Single mode fibres |
| OS | OS |
| BASE-LX | BASE-LX |
| BASE-LR/LW | BASE-LR/LW |
| BASE-ER | BASE-ER |
| BASE-FR | BASE-FR |

- A bandwidth calculation determines whether the bandwidth of the transmission link is sufficient for the planned applications.

- For multi-mode fibres, the bandwidth limit (BM) of the transmission link can be calculated based on the bandwidth-length product (BLP) [MHz*km] in accordance with the following formula:

  - BM = BLP / cable length

- Given their high transmission quality, calculating the BLP of single-mode cables is largely theoretical. Here, attenuation data are important.

- A range calculation can be performed based on an optical loss budget. For this purpose, the individual losses of the system must be added. This is shown in the following formula (table):

Figure 11: Calculation of the optical loss budget of optical fibre paths

| Eingekoppelte Leistung | Coupled power |
| --- | --- |
| Gemäß Datenblatt der verwendeten Komponente | IAW the data sheet of the component used |
| Abzüglich Reserve | Minus reserve |
| Für Alterung der optischen Sender und der Fasern sowie für Reparaturen ca 3 dB | For the ageing of optical transmitters and fibres and for repairs approx. 3 dB |
| Abzüglich LWL-Dämpfung | Minus loss of optical fibres |
| Länge x Dämpfung/km, gem. Datenblatt Kabelhersteller | Length x loss/km, IAW data sheet of cable manufacturer |
| Abzüglich Spleißdämpfung | Minus splice loss |
| Anz. Spleiße (m) x Dämpfung/Spleiß = 0,3 dB (EN 50173-1, Tab 65) | Number of splices (m) x loss/splice = 0.3 dB (EN 50173-1, table 65) |
| Abzüglich Steckerdämpfung | Minus connector loss |
| Anz. Stecker (n) x Dämpfung/Stecker = 0,75 dB (EN 50173-1, Tab 65) | Number of connectors (n) x loss/connector = 0.75 dB (EN 50173-1, table 65) |
| Anzüglich sonstiger Komponenten | Minus other components |
| Dämpfung sonstiger Komponenten oder Querschnittwechsel | Loss caused by other components or changes in cross-section |
| ERGIBT: Leistung am Empfänger | RESULTS IN: Output at receiver |
| Minimale Empfängerempfindlichkeit gemäß Datenblatt | Minimum receiver sensitivity IAW data sheet |

- All unarmoured communications cables and all fibre-optic cables can be installed in cable duct systems consisting of plastic pipes or concrete conduit bricks.

- In most Bundeswehr buildings, building distributors and floor distributors may be combined. In this case, a secondary region is not required. For this purpose, the distributor must be installed at a central position of the building.

- The secondary network is the connection inside the building between the building distributor and other distributors. Normally, it extends from the building distributor through to the floor distributors connected in a star-shaped manner. Fibre-optic cables must be used for these connections.

- In order to ensure mechanical protection (bending radius, rodents), all fibre-optic cables must be installed in appropriately labelled tubes (DN 25 – DN 40) or in closed ducts. The pipes must be marked with clearly visible red adhesive labels with the inscription “Achtung Lichtwellenleiter" (Caution! Fibre-optic cable!). An appropriate internal cable is included in the following table.

In this document: Figure 2

In this document: Figure 2

Figure 12: Guide values for internal cables in accordance with DIN EN 60794-2

| Innenkabel: Kabelaufbau und- Kennzeichnung gemäß DIN EN 60794-1-1, Beiblatt1: J-V(ZN)HH n x G50/125 OM4 bzw. E9/125 … OS2 | Internal cable: Cable design and marking IAW DIN EN 60794-1-1, Supplement 1: J-V(ZN)HH n x G50/125 OM4 and/or E9/125 … OS2 |
| --- | --- |
| Außen- und Einzelmantel flammhemmend und halogenfrei | Outer and single sheath fire-retardant and halogen-free |
| Zugentlastungselemente: nichtmetallisch | Strain relief elements: non-metallic |
| Farbkodierung der Einzelmantel und Kennzeichnung der Einzelkabel (z.B. durch Nummerierung) | Colour coding of single sheaths and marking of individual cables (e.g. by assigning numbers) |
| Weitere Eigenschaften, wie z.B. | Further features such as |
| Temperaturbereiche (Betrieb, Verlegung, Lagerung) | Temperature ranges (operation, laying, storage) |
| Minimale Biegeradien | Minimum bending radii |
| Maximale Zugbelastbarkeit | Maximum allowable tension |
| Maximaler Querdruck | Maximum lateral pressure |
| Kabeltorsion | Torsion |
| Schlagfestigkeit | Impact resistance |
| Multimode-Fasern | Multi-mode fibres |
| Werte siehe Tabelle13 | See table 13 for values |
| Singlemode-Fasern | Single mode fibres |

- Data cable connection technology, optical fibres

  - For new networks, the following sockets are to be used:

  - In the primary network: SC duplex connectors, in justified cases E2000 duplex connectors

  - In the secondary and tertiary networks SC duplex connectors

  - In active components also LC duplex connectors

- Requirements for fibre optic links:

  - Connector loss < 0.2 dB

  - Splice loss < 0.1 dB

  - Return loss (single-mode fibre) > 50 dB

  - Use of ceramic ferrules (due to their inferior transmission values, cheaper metal or plastic ferrules should not be used).

  - Because of their lower loss, fibre-optic connectors that have been prefabricated at the factory (pigtails) must be provided in the primary and secondary region and connected by means of fused splices.

- Care must be taken that protective caps are always put on all connectors for protection against dirt and mechanical damage.

Figure 13: Sample SC duplex and simplex connectors

Figure 14: Sample LC duplex connector

- As cable end boxes, fibre-optic patch panels with splice cassettes must be used. For the sake of accessibility, telescopic and, for ease of assembly, hinged or swiveling designs are to be used. The incoming cable must be protected by a strain relief against damage when pulling out the patch panel Within the splice holder, fibres must be sufficiently protected by means of cable holders.

- Depending on the cable design and the necessary cassettes for accommodating fibres and splices, thermoplastic screw-type clamping sleeves or thermoplastic clamping sleeves are used for the connection and branching off of fibre-optic cables as well as for the transition from fibre-optic outside cables to fibre-optic inside cables.

- Inside the central distribution boards of the facility, the cable routes are provided via separate routing systems and building inlets to the IT rooms.

- The tertiary network includes all connections between the building distributor (or floor distributor, in case there is a secondary network) and the terminal equipment connectors. Cable routing within these networks is always configured in a star-shaped manner from the distribution room to the terminal equipment.

- At present, the tertiary region has a standard transmission speed of 1 Gbit/s (1000BASE-T connection). This standard is downward compatible to 100BASE-T. The switch ports are designed for a transmission speed of 1 Gbit/s.

- In the tertiary region, symmetrical Screened Foil Twisted Pair (S/FTP) cables (overall copper braid screen, in pairs fitted with an aluminium foil screen, twisted in pairs) with four twin wires of at least category 7 which support 10GbE must be used.

- In order to be prepared for the increasing requirements of devices using Power-over-Ethernet (PoE), only American Wire Gauge 22 (AWG 22) cables or better, which corresponds to a conductor diameter ≥ 0.644 mm, are to be used.

- In the tertiary region, cable routes must not exceed 90 m.

Figure 15: Transmission link for balanced cabling

| Übertragungsstrecke | Transmission link |
| --- | --- |
| Verkabelungsstrecke | Cabling link |
| ASG | ASG |
| V | V |
| EE | EE |
| Geräteverbindungskabel | Device connecting cable |
| Rangierkabel | Patch cable |
| TA | TA |
| Geräteanschlusskabel | Device power cable |
| EV | Floor distributor |
| ASG (anwendungsspezifisches) Gerät im Etagenverteiler | ASG (application-specific) device in the floor distributor |
| V Verbindung | V connection |
| EE Endgerät am Arbeitsplatz | EE Terminal device at the workplace |
| TA informationstechnischer Anschluss | TA IT connection |
| 1) Mechanische Länge, entspricht 7,5 m elektrischer Tertiärverkabelung | 1) Mechanical length, equivalent to an electrical tertiary cabling of 7.5 m |
| 2) Gesamt 10 m mechanisch, 15 m elektrisch | 2) Total 10 m mechanical, 15 m electrical |

Figure 16: Fibre-optic transmission link

| Übertragungsstrecke | Transmission link |
| --- | --- |
| Verkabelungsstrecke | Cabling link |
| ASG | ASG |
| V | V |
| EE | EE |
| S | S |
| EV | Floor distributor |
| Abhängig von LWL-Typ | Depending on the fibre-optic cable type |
| ASG (anwendungsspezifisches) Gerät im Etagenverteiler | ASG (application-specific) device in the floor distributor |
| V Verbindung | V connection |
| S Spleiß | S splice |
| EE Endgerät am Arbeitsplatz | EE Terminal device at the workplace |

## Special requirements for communications cables / telephone lines

- In spite of the changeover of telecommunications to IP, dedicated electrical connections via classical communications cables (Cat 3 copper cables) are still required e.g. for emergency telephones and for the transmission of specific alerts in other networks.

- There must be a communication cable connection with at least 10 twin wires from the main communications distributor in or close to the central distribution board of the facility to every building distributor. In justified cases, these dimensions may be increased.

- The main distribution board consists of a vertical side for connecting the external lines and a horizontal side for connecting the telephone system and any other communications systems. The two sides of the main distribution board are connected with each other by jumper wires. On the vertical side of the main distribution board, it must be possible to separate lines and to switch on either test or measuring equipment.

- Solderless, screwless and stripless quick-connect designs must be used as termination devices for the vertical and horizontal sides. Profile rods (no mount frames) are to be used for installing LSA Plus disconnecting links for ease of inspection.

- The connection shall be routed via LSA Plus disconnecting links with overvoltage protection. Cabling [I-Y(ST)Y, 1x 50 double wires] must be provided from the LSA Plus panel in the telecommunications distributor to the Cat. 3 patch panel [25 x 4(8)] in the building distributor.

- The following (communications) cables must be used as standard cables for the Bundeswehr:

  - For underground installation or installation in cable protective pipes (standard): A-2YF(L)2Y x 2 x 0.6 mm St III Bd or x 2 x 0.8 mm St III Bd (DIN VDE 0816-1) (for larger distances: Cables with a copper conductor diameter of 0.9, 1.2 or 1.4 mm)

  - For aboveground installation (exception): A-2Y(St)2Y-T..x 2 x 0.6 mm or..x 2 x 0.8 mm [self-supporting open-air installed cable (span width, building / building)]

- Within the building, the underground copper cables of the IT network are terminated by joints. From there they are routed and connected by internal cables to the building distributor.

- The strand type of the internal cables must be adapted to the strand type of the underground cables.

## Special requirements for distribution cabinets / racks

- The distribution cabinets must be installed in a free-standing position in adequately dimensioned rooms.

- If the local conditions permit, it is also possible to use open 19” frames instead of closed cabinets. In this case, doors, side panels and cabinet ventilation are not required.

  - Height of cabinets: approximately 40 to 42 height units, width: 19 “; system cabinets (W x H x D = 800 x 2,120 x 1,000) - dimensions indicated in mm - are recommended as distribution cabinets. Front side and rear sides must be accessible. In case of small tertiary regions, distribution boards must be provided as required.

  - Cabinet depth: 1,000 mm State-of-the-art active components require larger dimensions (e.g. due to PoE). It is already foreseeable that cabinet depths of 1,200 mm will be required in the future.

  - 250 V, 50 Hz power supply by two firmly installed, permanently connected and not switchable multiple socket outlets, each comprising 6 sockets and two separate circuits and Type III overvoltage protection devices; if the sockets in the cabinet are not protected by an RCD, the operator has to specify measures to permanently rule out the general use of these sockets within the framework of a job hazard analysis in accordance with the Betriebssicherheitsverordnung (Operational Safety Ordinance) (see DIN VDE 0100-410:2018-10, para 411.3.3). In addition, the sockets must be labelled “nicht über RCD abgesichert" (not protected by a residual current device (RCD)).

  - As soon as active LAN components (e.g. switches) and terminal equipment (e.g. VolP telephones) with PoE (15 W), PoE+ (30 W) - in accordance with standard IEEE 802.3at - are used, the energy requirement must be determined and the number of circuits must be increased accordingly. In this case, the power is transmitted through four wires (two pairs) of an Ethernet cable (at least category 5e). The new standard IEEE 802.3bt describes PoE++, which introduces new power levels 45 W, 60 W, 75 W and 90 W, with the power being transmitted through four pairs of the Ethernet cable. When selecting the type of installation, the heating of the cable caused by a high-performance PoE must be taken into account.

  - Earthing, protective equipotential bonding, functional equipotential bonding (see also para 5.4.4.3) All electrically conductive parts of the cabinets (including doors) must be connected with each other and with an equipotential bonding bar, which must be as high as the cabinet, by a copper conductor with a minimum diameter of 4 mm². The casings and earth connections of the devices and the patch panels for data copper cables must be connected individually / in a star-shaped manner by 6 mm² copper conductors to the next equipotential bonding bar using the shortest route (max. 50 cm). Two copper bars, which must be as high as the cabinet and should preferably be supplied by the manufacturer of the cabinet, must be used as equipotential bonding bars in the cabinet. They must be connected with each other by a 16 mm² copper wire. The second bar is necessary for fulfilling the requirements of functional-equipotential bonding and electromagnetic compatibility. The equipotential bonding bar of the cabinet must be connected to the next connector of the building’s protective-equipotential bonding system located in the same room by a 16 mm² copper wire. Note: The removal of electrical connections must not be possible without the aid of a tool.

  - Door lock with uniform lock cylinder.

  - 19 “mounting frame to the front and rear.

  - removable side panels

  - Cable routing brackets on both sides. (Minimum depth of bracket: 125 mm)

  - Adequate patch panel (Minimum depth of bracket: 105 mm)

  - Wiring plan pocket

  - Telescopic pull-out shelf for depositing measuring instruments or as a pad

  - Cable entry either from above or from below

  - Base (at least 10 cm)

  - Lateral cable routing duct for fibre-optic patch cables

  - C profile rails for mounting data cables (front and rear 19” area must be kept clear)

  - As required: Cabinet lighting including fragmentation protection / front and rear cover of lamp, with door contact; internal cabinet lights provided by the cabinet supplier must be used.

  - For aeration, cooling, air-conditioning see para 5.3.

- In the decentralised area (not in distribution rooms), less active components including connections and accessories may also be installed in wall-mounted cabinets in exceptional, duly justified cases and in coordination with the operator. In this connection, it should be noted that these cabinets must not be mounted high on the wall (bottom edge ≥ 2 m above floor level) in order to avoid additional protective measures and an unnecessary increase in maintenance effort due to the requirement of ladders / movable scaffoldings with manual protective devices. In addition, the applicable industrial safety regulations for wall-mounted cabinets must be observed (e.g. risk of head bump injuries).

- The use of swivel rack mounts is not permissible because of the torsion stress imposed on the cables during the swivelling movement.

- If the use of a swivel rack mount is - due to very confined local conditions - absolutely necessary for the maintenance of the active components, the cabinet must be divided into two parts. In the upper part of the cabinet, the active components must be installed on a swivel rack mount with an adequately low installation height. In the bottom part of the cabinet, all patch panels must be attached to permanently installed 19” bars. A reserve capacity of 25 % must be included for subsequent extensions. The bottom part of the cabinet may be equipped with a swivel rack mount with an adequately low installation height. It should be noted that four to eight height units are lost if a swivel rack mount is installed.

- If a building automation system is available and cooling systems are used, the reports (group error, actual temperature) of these systems must be transmitted to that point.

- The following figures show an exemplary layout of an IT network cabinet.

Figure 17: Server cabinet, front view

| Lüfterdach | Fan top cover |
| --- | --- |
| LWL-Patchfeld 12 x SC-duplex (24 Fasern) | Fibre optic patch panel 12 x SC duplex (24 fibres) |
| Reserve leer | Reserve empty |
| Aktive Komponente (z.BB. Switch) Kabelführung 105 mm | Active component (e.g. switch) cable ducting 105 mm |
| Profilschiene mit Kabelbügel und Gegenwanne | Profile rail with cable bracket and clamping saddles |
| Verteilerfeld 24 x RJ45 CAT 6A | Distributor panel, 24 x RJ45 CAT 6A |
| Kabelführung 105 mm | Cable ducting 105 mm |
| Rangierbügel | Cable management bracket |
| USV mit Controller und Batterie | UPS with controller and battery |
| Sockel | Base |
| USV Batterie | UPS battery |
| USV / Controller | UPS controller |
| Reserveplatz Verteilerfeld mit Kabelführung | Vacant position distributor panel with cable routing |
| Reserveplatz Aktivkomponenten | Vacant position, active components |
| Steckdosenleisten 2x6-fach mit Überspannungsschutz (SPD II) und Festanschluss Mitte Schrank | Multiple socket outlets 2x 6, with overvoltage protection (SPD II) and fixed connection in the middle of the cabinet |

Figure 18: Server cabinet, side view

| Lüfterdach | Fan top cover |
| --- | --- |
| LWL-Patchfeld 12 x SC-duplex (24 Fasern) | Fibre optic patch panel 12 x SC duplex (24 fibres) |
| Aktive Komponente | Active component |
| Kabelführung 105 mm | Cable ducting 105 mm |
| Rangierbügel | Cable management bracket |
| Reserveplatz Aktivkomponenten | Vacant position, active components |
| 2 x Steckdosenleiste Anordnung Mitte Schrank | 2x multiple socket outlet, in the middle of the cabinet |
| N x Verteilerfeld 24x RJ45 CAT 6A | Nx distributor panel 24x RJ45 CAT 6A |
| 1 x Verteilerfeld 25x8(4) RJ45 CAT 3 | 1x distributor panel 25x8(4) RJ45 CAT 3 |
| Reserveplatz Verteilerfeld mit Kabelführung | Vacant position, distributor panel with cable routing |
| 2x CU-Schiene für Potenzialausgleich | 2x equipotential bonding copper bar |
| 16mm² Potenzialausgleich zu Pot.-Schiene im Raum | 16 mm² equipotential bonding to equipotential bonding bar in room |
| USV Controller | UPS controller |
| USV Batteriepack | UPS battery pack |
| Sockel | Base |
| Abzweigdosen für Direktanschluss Steckdosenleisten | Junction box for direct connection of multiple socket outlets |

Figure 19: Server cabinet, top view

| Aktive Komponente (Switch) | Active component (switch) |
| --- | --- |
| LWL-Spleißbox | Fibre optic splice box |
| RJ45-Patchfeld | RJ45 patch panel |
| Frontseite | Front end |
| C-Profil | C profile |

- In order to accommodate active components and provide sufficient patch space, the cabinet must have a floor area of at least 800 mm width x 1,000 mm depth. Standard cabinets usually have a height of 41 or 42 height units, which corresponds to approximately 2.2 m. As a rule, smaller cabinets with a height of 21 height units are sufficient for buildings with a requirement of 24 or less active ports.

- In order to facilitate the regeneration of active components, free mounting slots should be provided between the active components, if possible.

- For the installation of active components sufficient space, which must be determined based on the current requirements and include an additional reserve of 25 %, must be provided.

- If the central distribution board of the facility serves as building distributor as well, it must also be equipped with a Cat. 3 RJ45 patch panel and a communications cable with 50 double wires as connection to the main communications distributor.

- Copper patch and connecting cables

  - Patch cables must be procured for 50 % (guide value) of the connections when the distribution boards are set up for the first time, colour: grey. Patch and connecting cables must be tailored to the type of the installation cable. This means that they must be of the same design (see DIN EN 50173-1, Aufbauarten symmetrischer Kupferkabel).

  - The length of the cables is to be coordinated with the operator prior to procurement.

  - The overall length of all patch and connecting cables of one transmission link must not exceed 10 m!

  - The minimum diameter of the wires for patch cables is AWG 26.

## Special requirements for other networks

- Hazard detection system: Hazard detection systems within buildings are operated separate from the IT networks (data / telecommunication networks). It has to be ensured that networks for fire alarms and for detecting other dangers are set up as physically and functionally separate networks.

- As a rule, the wiring of hazard detection systems within buildings must be routed separately in accordance with the system-specific provisions and standards. Within buildings, networks are usually established with copper cables.

- Between buildings, the existing fibre optic cables of the IT network are to be used preferably. Optical fibres used for hazard detection systems are to be spliced up to the security facilities. Patches in IT distributors are to be avoided. The required optical fibres will be provided by BWI for the buildings to be supported by BWI.

- Central facilities for hazard detection reports must not be generally accessible.

- Intrusion detection systems: There might be a requirement for alert messages to be transmitted via copper cables (communications cables).

- Fire detection and fire alarm systems: The minimum components of a fire detection and fire alarm system are specified and defined in DIN EN 54-1.

- For fire detection and fire alarm systems, only systems should be used that have been tested and approved by an accredited authority or certified regarding their conformity.

- The fire detection and fire alarm system must be operated within the buildings via a separate network. Fan-out units must be marked in red on the inside. If lines are routed through fan-out units of other communication service providers, connection clamps are to be marked in red.

- In order to keep the risk of damage to cables low, lines must be laid and fixed with adequate mechanical protection. The number of line connections should be kept as low as possible. Each line connection must be soldered or made by mechanically reliable electrical connectors (e.g. LSA-Plus).

- Statically insulated installation cables (J-Y(St)Y ...x2x0,n) with a duct diameter of at least 0.6 mm are to be used for fire detection and fire alarm system networks.

- Lines must be used which are labelled with the imprint “BRANDMELDEKABEL” (FIRE ALARM CABLE) in red letters on the braid line. Cables may be installed either on plaster or under plaster in dry and damp rooms.

- Building automation system: For new systems, building automation systems are usually networked via the LAN with TCP/IP. In that case, the IT network-connecting box (one port, top hat rail mounting) is installed in the building automation cabinet of the respective building.

- When dimensioning the connection between the building distributors und the building connections within the facility with fibre optic cables, four optical fibres must be provided for parallel cable routing and separate ports are to be provided in the IT distributors for the building automation systems.

- Time recording, access control: The peripheral equipment such as time recording systems and ID card readers are equipped with system-specific interfaces or data ports. Instead of the telephone cables used so far (e. g. JY(St)Y), category 7 data cables are to be employed.

- The central components usually communicate via Ethernet-TCP/IP. A separate VLAN is to be set up.

- If conventional technology is used, the IT network must be used in the primary region.

- TV antenna assembly (satellite / terrestrial): Setting up a central head end, using the fibre-optic primary network as well as using the IT network in the tertiary area (by means of adequate conversion devices) is often more reasonable and economical in the long term than setting up a facility network with coaxial cables or installing individual systems in each building.