# Room layout plan

- Sample facility access node / distribution node

| LAN | LAN |
| --- | --- |
| LAN (Reserve) | LAN (reserve) |
| Fm-HVt | Main communications distributor |
| Kälte Klima | Cooling, air conditioning |
| Carrier | Carrier |
| WAN | WAN |
| TK | Kitchenette |
| USV | UPS |
| APL-Carrier | Demarcation point carrier |
| UV-IT-USV | IT sub-distributor (UPS) |
| UV-AV | General power supply sub-distributor |

2.1.	Facility distribution node	2

2.2.	Building distributor	7

2.3.	Floor distributor	10

# Structural and technical space requirements

## Facility distribution node

- Room size of facility access node: approx. 35 m²

- 2 facility access nodes (redundancy) at different sides of the facility (edge disjoint)

- Integration of the demarcation point (= transfer point to the WAN) and of the central layer-3 switch (LAN core)

- Transverse connections of the WAN and LAN components on separate routes

- No redundancy is required for ventilation and air-conditioning in the individual facility access nodes

| ID no. | Item | Quantity | Specifications | Remarks |
| --- | --- | --- | --- | --- |
|  | Room temperature |  | Between 19 and 22 °C | Adjustable temperature ranges |
|  | Lighting |  | Min. 500 lx |  |
|  | Power supply | 6 | Type F sockets (CEE 7/3 – double-pole sockets with protective earth contact, AC, 16 A, 250 V, 50 Hz) | The power sub-distributor must be integrated in the facility access node; power supply for server cabinets must be ensured from above, or, in case of raised bottoms, from below. |
|  | Power supply at the server cabinet | 2x 6 per cabinet | Type F sockets (CEE 7/3 – double-pole sockets with protective earth contact, AC, 16 A, 250 V, 50 Hz) | Firmly installed, not switchable multiple socket outlets at two separate circuits; type III overvoltage protection devices |
|  | Window(s) |  |  | Not required |
|  | Doors |  |  | Threshold- / barrier-free, soundproof door, at least 1,000 mm x 2,100 mm, fire-retardant, lockable, external knob |
|  | Floors |  | light-coloured | Anti-static, flame-resistant, noice-reducing, easy to clean, heat insulated, shock-absorbing, elastic |
|  | Walls/ceilings |  | Light-coloured paint | level, smooth, light-coloured, washable, resistance class RC 3 |
|  | Ventilation |  |  | Artificial ventilation |
|  | Cooling / air conditioning |  |  | Required; if no central cooling is available, split air conditioning units may be used. Air conditioning units must be supported by uninterruptible power supply and carry out automatic restarts in case of failure. |
|  | Uninterruptible power supply (UPS) |  | Required | Air conditioning unit(s), supplying / extracting air, all active IT components. The diagram in figure 34 must be observed. UPS via a separate branch of the sub-distribution; IT components via separate branches after the UPS In construction planning, UPS must be designed to provide emergency power in case of power outages of up to 180 min if there is no emergency power system. UPS must be designed with an external bypass. |
|  | UPS batteries |  | Required | In a place as cool as possible in the facility access node (optimum temperature ~ 20 °C) |
|  | Telephone connection | 1 |  | The main communications distributor must be integrated in the facility access node. |
|  | Carrier connection |  |  | Via separate routes to the individual facility distribution nodes |
|  | Earthing |  |  | Earthing of distribution cabinets required; all server cabinets must be connected via copper cable with a minimum diameter of 4 mm², 2 equipotential bonding bars; bleeder resistance ≤ 108 Ω |
|  | IT port |  | Optical fibre, CAT 7 (exception) | The facility distribution node must be connected to the WAN via optical fibres with the primary route consisting of single-mode (at least OS2) or multi-mode fibres (at least OM4). The bending radii specified by the manufacturer must be observed. |
|  | Telephone cables |  | Copper cables | Communications link between the main communications distributor and the building distributors with at least10 twin wires |
|  | Fire detection and fire alarm system |  |  | Earliest detection system, alert must be transmitted to a central element (e.g. guard building) |
|  | Intrusion detection system |  |  | Must be included in planning, with alerts being transmitted to a central element (e.g. guard building) |
|  | Base |  |  | In the facility distribution node, all cabinets must be placed on bases. Alternative: Raised floor |
|  | Overvoltage protection |  | Primary protection for IT and communications cables in the immediate vicinity of the building inlet | - • Nominal DC spark-over voltage: VsdcN = 230 V - Nominal alternating discharge current: IdaN = 2.5 A or 10 A - Nominal impulse discharge current: idiN = 2.5 A or 10 kA |

| GA | Building automation |
| --- | --- |
| Kälte Klima | Cooling, air conditioning |
| Elektro UV-AV | Power sub-distributor, general supply |
| Optional | As required: |
| Elektro-NSHV | Main low-voltage distribution frame |
| NEA | Emergency power system |
| Elektro UV-IT (USV) | IT sub-distributor (UPS) |
| USV | UPS |
| VolP TK-Anlage | VolP telecommunications system |
| Fm-HVt | Main communications distributor |
| Liegenschaft n x Gebäude | Facility n x building |
| APL | Demarcation point |
| Carrier | Carrier |
| WAN | WAN |
| LAN | LAN |
| LWL-Primärnetz Liegenschaft n x Gebäude | Fibre-optic primary network n x building |
| Übersichtsschema LVt-Raum | Basic diagram of facility distribution room |

| Reserve | Reserve |
| --- | --- |
| UV-IT (USV) | IT sub-distributor (UPS) |
| UV-AV | General power supply sub-distributor |
| Online-USV (statistischer Bypass) | Online UPS (static bypass) |
| Externer Bypass (Handumgehung) | External bypass (manual bypass) |
| IT-Rack | IT rack |
| Lüftung | Ventilation |
| Kälte | Cooling |
| GA | Building automation |
| Bel. | Random |
| Allg. | General |
| NSHV-AV | Main low-voltage distribution frame - general power supply |
| Einspeisung über Allgemeinnetz (Trafo) | Supply via general network (transformer) |
| Einspeisung über NEA | Supply via emergency power system |
| Stromversorgungsprinzip LVt-IT-Raum | Power supply principle, facility distribution IT room |

## Building distributor

- 1 building distributor per building, feeding of the 2 facility distribution nodes via 2 separate cable routes (distance between routes at least 2 m - cf. network SOR)

- Access restriction system required

- Dry room

- • Situation

- + Not to be located near transformers or lifts (due to electromagnetic vulnerability)

- + Not to be located in the immediate vicinity of rooms with a high fire load

- + Symmetrical (at equal distance) to recorded building components

- + If possible, not next to heating rooms

- + No water and / or heating pipes in the IT distribution room; existing water-carrying pipes shall be sealed up

- + External heat sources are to be avoided

- + No windows, if possible; otherwise orientation of the windows towards the north

- • Minimum room size 6 m², minimum height 2.5 m, see table 18

- • Doors with an internal frame dimension of at least 90 cm

| ID no. | Item | Quantity | Specifications | Remarks |
| --- | --- | --- | --- | --- |
|  | Room temperature |  | Between 19 and 26 °C | Adjustable temperature ranges |
|  | Lighting |  | Min. 500 lx |  |
|  | Power supply | 6 | Type F sockets (CEE 7/3 – double-pole sockets with protective earth contact, AC, 16 A, 250 V, 50 Hz) | Power supply for server cabinets must be ensured from above, or, in case of raised bottoms, from below; in the server cabinet 2x 6 sockets fed by 2 separate circuits At least 2x double socket 230 V, 50 Hz |
|  | Window(s) |  |  | Not required |
|  | Doors |  |  | Threshold- / barrier-free, soundproof door, at least 1,000 mm x 2,100 mm, fire-retardant, lockable, external knob |
|  | Floors |  | light-coloured | anti-static, flame-resistant, noise-reducing, easy to clean, heat insulated, shock-absorbing, elastic, bleeder resistance ≤ 108 Ω |
|  | Walls/ceilings |  | Light-coloured paint | level, smooth, light-coloured, washable, resistance class RC 3 |
|  | Ventilation |  |  | Artificial ventilation |
|  | Cooling / air conditioning |  |  | Required; if no central cooling is available, split air conditioning units may be used. Air conditioning units must be supported by uninterruptible power supply and carry out automatic restarts in case of failure. |
|  | Uninterruptible power supply (UPS) |  | Required | Power outage backup time 180 minutes, if no emergency power system is available, UPS for air conditioning and emergency lighting must be provided, server UPS may be accommodated in the server, if required. |
|  | UPS batteries |  | Required | In a place as cool as possible in the facility access node (optimum temperature ~ 20 °C) |
|  | Telephone connection | 1 |  |  |
|  | Carrier connection |  |  | Via separate routes to the individual building distributors |
|  | Earthing |  |  | Distribution cabinets must be earthed; 2 equipotential bonding bars |
|  | IT port |  | Optical fibres or xDSL CAT 7 (exception) | Building distributors must be connected (separate routes) to the facility distribution nodes via optical fibres with single-mode (at least OS2) or multi-mode optical fibres (at least OM4). The bending radii specified by the manufacturer must be observed. For buildings with a small number of connections, xDSL technology may be used. |
|  | Telephone cables |  | Copper cables | Telephone connections are to be routed via the building distributor to the floor distributors. |
|  | Fire detection and fire alarm system |  |  | Earliest detection system, alert must be transmitted to a central element (e.g. guard building) |
|  | Intrusion detection system |  |  | Must be included in planning, with alerts being transmitted to a central element (e.g. guard building) |
|  | Base |  |  | In the facility distribution node, all cabinets must be placed on bases. Alternative: Raised floor |
|  | Overvoltage protection |  | Primary protection for IT and communications cables in the immediate vicinity of the building inlet | - • Nominal DC spark-over voltage: VsdcN = 230 V - Nominal alternating discharge current: IdaN = 2,5 A or 10 A - Nominal impulse discharge current: idiN = 2.5 A or 10 kA |

## Floor distributor

- No floor distributors are required if power supply can be ensured via the building distributor.

- 1 building distributor per building, feeding of the 2 facility distribution nodes via 2 separate cable routes (distance between routes at least 2 m - cf. network SOR)

- Access restriction system required

- Dry room

- • Situation:

  - + Not to be located near transformers or lifts (due to electromagnetic vulnerability)

  - + Not to be located in the immediate vicinity of rooms with a high fire load

  - + Symmetrical (at equal distance) to recorded building components

  - + If possible, not next to heating rooms

  - + No water and/or heating pipes in the IT distribution room; existing water-carrying pipes are to be sealed off

  - + External heat sources are to be avoided

  - + No windows, if possible; otherwise orientation of the windows towards the north

  - • Minimum room size 6 m², minimum height 2.5 m, see table 18

  - • Doors with an internal frame dimension of at least 90 cm

| ID no. | Item | Quantity | Specifications | Remarks |
| --- | --- | --- | --- | --- |
|  | Room temperature |  | Between 19 and 26 °C | Adjustable temperature ranges |
|  | Lighting |  | Min. 500 lx |  |
|  | Power supply | 6 | Type F sockets (CEE 7/3 – double-pole sockets with protective earth contact, AC, 16 A, 250 V, 50 Hz) | Power supply for server cabinets must be ensured from above, or, in case of raised bottoms, from below; in the server cabinet 2x 6 sockets fed by 2 separate circuits At least 2x double socket 230 V, 50 Hz |
|  | Window(s) |  |  | Not required |
|  | Doors |  |  | Threshold- / barrier-free, soundproof door, at least 900 mm x 2,100 mm, fire-retardant, lockable, external knob |
|  | Floors |  | light-coloured | anti-static, flame-resistant, noise-reducing, easy to clean, heat insulated, shock-absorbing, elastic Bleeder resistance ≤ 108 Ω |
|  | Walls/ceilings |  | Light-coloured paint | level, smooth, light-coloured, washable, resistance class RC 3 |
|  | Ventilation |  |  | Artificial ventilation |
|  | Cooling / air conditioning |  |  | Required; if no central cooling is available, split air conditioning units may be used. Air conditioning units must be supported by uninterruptible power supply and carry out automatic restarts in case of failure. |
|  | Uninterruptible power supply (UPS) |  | Required | Power outage backup time 180 minutes, if no emergency power system is available, UPS for air conditioning and emergency lighting must be provided, server UPS may be accommodated in the server, if required. |
|  | UPS batteries |  | Required | In a place as cool as possible in the facility access node (optimum temperature ~ 20 °C) |
|  | Telephone connection | 1 |  | . |
|  | Earthing |  |  | Distribution cabinets must be earthed; 2 equipotential bonding bars |
|  | IT port |  | Optical fibres or xDSL CAT 7 (exception) | Floor distributors must preferably be connected (separate routes) to facility distribution nodes via single-mode (at least OS2) or multi-mode fibres (at least OM4). The bending radii specified by the manufacturer must be observed. For buildings with a small number of connections, xDSL technology may be used. |
|  | Telephone cables |  | - J-Y(St)Y …..Bd duct diametre 0.6 or 0,8 mm. CAT 7 from floor distributor to the rooms to be connected | Communication cable connection from the floor distributor to the building distributer via LSA Plus disconnecting links with I-Y(ST)Y cable. Cable dimensions as required (plus reserve). The connection is to be routed via LSA Plus links, from the LSA Plus panel to the Cat. 3 patch panel in the floor connector [25 x 4(8)]. Cabling must be provided in the building distributor [I-Y(ST)Y, 1 x 50 twin wires]. A communications cable of the following type is to be installed: - J-Y(St)Y …..Bd duct diametre 0.6 or 0,8 mm. |
|  | Fire detection and fire alarm system |  |  | Earliest detection system, alert must be transmitted to a central element (e.g. guard building) |
|  | Intrusion detection system |  |  | Must be included in planning, with alerts being transmitted to a central element (e.g. guard building) |
|  | Base |  |  | In the floor distributor, all cabinets must be placed on bases. Alternative: Raised floor |
|  | Overvoltage protection |  | Primary protection for IT and communications cables in the immediate vicinity of the building inlet | - • Nominal DC spark-over voltage: VsdcN = 230 V - Nominal alternating discharge current: IdaN = 2,5 A or 10 A - Nominal impulse discharge current: idiN = 2.5 A or 10 kA |

# Furnishings:

Furniture and equipment

Facility access node:

| ID no. | Item | Quantity | Remarks |
| --- | --- | --- | --- |
|  | Server cabinet, height x width x depth in mm 2,120 x 800 x 1,000 | 3 | These are minimum dimensions. The cabinet might as well have a depth of 1,200 mm 42 height units, width 19”, lockable at the front and rear |
|  | Table (120 cm x 80 cm) | 1 | For console workstation |
|  | Office swivel chair | 1 | For console workstation |
|  | 1x shelf, height x width x depth at least 200 cm x 120 cm x 60 cm |  |  |

Building distributor:

| ID no. | Item | Quantity | Remarks |
| --- | --- | --- | --- |
|  | Server cabinet, height x width x depth in mm 2,120 x 800 x 1,000 | 1 | These are minimum dimensions. The cabinet might as well have a depth of 1,200 mm 42 height units, width 19”, lockable at the front and rear |
|  | 1x shelf, height x width x depth at least 200 cm x 120 cm x 60 cm |  |  |

Floor distributor:

| ID no. | Item | Quantity | Remarks |
| --- | --- | --- | --- |
|  | Server cabinet, height x width x depth in mm 2,120 x 800 x 1,000 | 1 | These are minimum dimensions. The cabinet might as well have a depth of 1,200 mm 42 height units, width 19”, lockable at the front and rear |
|  | 1x shelf, height x width x depth at least 200 cm x 120 cm x 60 cm |  |  |

| Lüfterdach | Fan top cover |
| --- | --- |
| LWL-Patchfeld 12 x SC-duplex (24 Fasern) | Fibre optic patch panel 12 x SC duplex (24 fibres) |
| Reserve leer | Reserve empty |
| Aktive Komponente (z.BB. Switch) Kabelführung 105 mm | Active component (e.g. switch) cable ducting 105 mm |
| Profilschiene mit Kabelbügel und Gegenwanne | Profile rail with cable bracket and clamping saddles |
| Verteilerfeld 24 x RJ45 CAT 6A | Distributor panel, 24 x RJ45 CAT 6A |
| Kabelführung 105 mm | Cable ducting 105 mm |
| Rangierbügel | Cable management bracket |
| USV mit Controller und Batterie | UPS with controller and battery |
| Sockel | Base |
| USV Batterie | UPS battery |
| USV / Controller | UPS controller |
| Reserveplatz Verteilerfeld mit Kabelführung | Vacant position distributor panel with cable routing |
| Reserveplatz Aktivkomponenten | Vacant position, active components |
| Steckdosenleisten 2x6-fach mit Überspannungsschutz (SPD II) und Festanschluss Mitte Schrank | Multiple socket outlets 2x 6, with overvoltage protection (SPD II) and fixed connection in the middle of the cabinet |
| IT-Netzwerkschrank (Frontansicht) | IT network cabinet (front view) |

| Lüfterdach | Fan top cover |
| --- | --- |
| LWL-Patchfeld 12 x SC-duplex (24 Fasern) | Fibre optic patch panel 12 x SC duplex (24 fibres) |
| Aktive Komponente | Active component |
| Kabelführung 105 mm | Cable ducting 105 mm |
| Rangierbügel | Cable management bracket |
| Reserveplatz Aktivkomponenten | Vacant position, active components |
| 2 x Steckdosenleiste Anordnung Mitte Schrank | 2x multiple socket outlet, in the middle of the cabinet |
| N x Verteilerfeld 24x RJ45 CAT 6A | Nx distributor panel 24x RJ45 CAT 6A |
| 1 x Verteilerfeld 25x8(4) RJ45 CAT 3 | 1x distributor panel 25x8(4) RJ45 CAT 3 |
| Reserveplatz Verteilerfeld mit Kabelführung | Vacant position, distributor panel with cable routing |
| 2x CU-Schiene für Potenzialausgleich | 2x equipotential bonding copper bar |
| 16mm² Potenzialausgleich zu Pot.-Schiene im Raum | 16 mm² equipotential bonding to equipotential bonding bar in room |
| USV Controller | UPS controller |
| USV Batteriepack | UPS battery pack |
| Sockel | Base |
| Abzweigdosen für Direktanschluss Steckdosenleisten | Junction box for direct connection of multiple socket outlets |
| IT-Netzwerkschrank (Seitenansicht) | IT network cabinet (side view) |

Due to the high number of IT devices, this room may have to be air-conditioned.

Due to the high number of IT devices, this room may have to be air-conditioned.

Due to the high number of IT devices, this room may have to be air-conditioned.