TECHNICAL SPECIFICATION

- DEFINITIONS AND ABBREVIATIONS

  - “Buyer” shall mean UAB Vilniaus kogeneracinė jėgainė

  - “Supplier” shall mean an economic operator, i.e. a natural person, a private legal person, a public legal person, other organisations and their subdivisions, or a group of such persons with whom the Buyer concludes a Contract.

  - “Contract” shall mean the Contract concluded between the Supplier and the Buyer in respect of the object of the Procurement.

  - “Goods” shall mean biomass ammonia measurement system.

  - „Services“ shall mean installation, connection, commissioning, and calibration of the biomass ammonia measurement system.

  - “Order” shall mean a written document provided to the Supplier on the basis of the Contract by text message, e-mail and/or through the information system specified by the Buyer, specifying the quantities of the Goods, the delivery addresses and the delivery date.

- OBJECT OF THE PROCUREMENT

  - Biomass ammonia measurement system and its installation

- SCOPE OF THE OBJECT OF THE PROCUREMENT

  - The quantities of Goods and Services are presented in Table No. 1 below."

Table No. 1

| Item No | Name of Goods / Services | Unit of Measure | Quantity for the Duration of the Contract |
| --- | --- | --- | --- |
| 1. | Biomass ammonia measurement system and its installation | pcs. | 2 |
| 2. | Installation, commissioning and calibration works | pcs. | 2 |

- PLACE OF PERFORMANCE OF THE CONTRACTUAL OBLIGATIONS

  - The Goods shall have to be delivered, and Services shall provided to the adress: Jočionių g. 13, LT-02300 Vilnius, Lithuania.

- REQUIREMENTS FOR THE OBJECT OF THE PROCUREMENT

Description of the Object of the Procurement

  - NH₃ concentration sensors must be installed for two biomass boilers.

  - The analysers shall be installed downstream of the boiler on the flue gas duct, upstream of the air preheater (see Figure No. 1), and prior to the flue gas treatment system.

Figure No. 1. Measurement points located on the flue gas duct upstream of the air preheater

  - The preliminary installation points for the NH₃ concentration analysers are indicated in Figure No. 1 and Table No. 2. Cross-sectional drawings of the available flanges are provided in Figures No. 2 and No. 3.

Table No. 2

| No. | Description | Level | Inclination |
| --- | --- | --- | --- |
| S1 | Nozzle reserve | +22,76 m | 0o |
| S2 | Nozzle reserve | +22,76 m | 0o |
| S5` | Nozzle reserve | +22,31 m | 10o |
| S5`` | Nozzle reserve | +22,31 m | 10o |
| S6 | Nozzle reserve | +22,06 m | 10o |

Figure No. 2 Nozzle No. S5`, S5``, S6, DN100PN6

Figure No. 3 Nozzle No. S1, S2, DN125PN6

  - The Supplier shall be responsible for connecting the equipment to the flue gas duct. If additional installation points and flanges are required for connecting the equipment, these shall be provided by the equipment supplier. The Buyer shall be responsible for their proper installation and welding.

  - The requirements for the Biomass Ammonia Measurement System are specified in Table No. 3.

Table No. 3

| Item No. | Equipment | Technical specifications and requirements |
| --- | --- | --- |
| 1. | Sample collection device | Ammonia samples must be collected automatically; The equipment must have protection against external influences and protection against contact; The measuring equipment must be resistant to temperatures up to 180°C; Power supply: 230 V. |
| 2. | Gas analyzer | Designed for continuous monitoring of NH₃ gases; Measurement is performed using Tunable Diode Laser Spectrometry (TDLS) method; Gas measurement is carried out based on an extractive principle; Measurement range: 0–10 / 0–50 mg/Nm³; Touch screen and navigation keyboard; Measurement accuracy not greater than ± 2% full range; Outputs: Analog signal 4...20 mA; Network connection with integrated ModBus or an equivalent protocol. |

  - The following media are possible at the measurement location, as presented in Table No. 4. The specified design measurement parameters, boiler load conditions, and scenarios for suitable and poor fuel are provided.

Tablr No. 4

| No. | Specification | Unit of Measure | Fuel according to the project |  |  | Fuel Biomass fuel – poor scenario |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Boiler load | % | 100 | 80 | 40 | 100 | 80 | 40 |
| 1. | Flue gas flow upstream of the air preheaters | m3/s | 53,34 | 44,9 | 30,43 | 57,32 | 49,5 | 33,13 |
| 2. | Temperature of the economizer stages | Co | 253 | 225 | 204 | 257 | 230 | 210 |
| 3. | Particulate matter downstream of the boiler | mg/ m3 @6% O2 | 1922 | 1822 | 1924 | 11408 | 11370 | 11786 |
| 4. | CO concentration in the flue gas downstream of the boiler | mg/ m3 @6% O2 | 160 | 160 | 160 | 160 | 160 | 160 |
| 5. | SO₂ concentration in the flue gas downstream of the boiler | mg/ m3 @6% O2 | 74 | 74 | 74 | 493 | 493 | 493 |
| 6. | NH₃ concentration in the flue gas downstream of the boiler | mg/ m3 @6% O2 | 10 | 10 | 10 | 10 | 10 | 10 |

  - After the equipment is installed, the Supplier shall perform the equipment calibration as required by the manufacturer's instructions.

  - The Supplier shall train the Buyer’s employees (at least 8 people) on how to operate the installed equipment and perform its maintenance.

  - The training shall be conducted at the Buyer’s premises. The training schedule and other related conditions must be agreed upon in advance with the Buyer.

- PROCEDURE AND TIME LIMITS FOR DELIVERY OF THE GOODS AND PERFORMANCE OF THE SERVICES

  - The Goods must be delivered no later than 80 (eighty) day from the date of placing the Order to the Supplier.

  - The Services must be provided no later than 14 (fourteen) day from the date of placing the Order to the Supplier.

  - The Supplier shall deliver the Goods and provided Services to the address specified in Section 4 of the Technical Specification during the Buyer’s working hours (I-IV 7:30 a.m. – 4:30 p.m., V 7:30 a.m. – 3:15 p.m.),

  - Goods will be delivered and Services will be provided only in accordance with individual Orders submitted by the Buyer during the term of the Contract.

  - A period of 5 (five) working days is set within which the Buyer must accept the provided Services (i.e. sign the handover-acceptance act).

- QUALITY AND REMEDYING DEFICIENCIES

  - The warranty period for the Goods shall be determined by the Supplier or the Manufacturer of the goods (with the longer applicable period being set), but in any case, it shall not be shorter than a 12 (twelve) month warranty period, calculated from the date of signing the Goods Transfer-Acceptance Act.

  - A 10 (ten) working day period is set to eliminate any defects noticed during the Goods / Services transfer-acceptance or warranty period, starting from the Buyer’s notification of faulty, defective, or substandard Goods / Services. The Supplier must, at their own expense, collect the defective/damaged Goods from the addresses specified by the Buyer and return the repaired Goods to the Buyer’s specified addresses from which they were collected, at the Supplier's own expense.

  - The Supplier shall certify that the sold Goods are fit for their intended use – if any – as stated in the Contract and that there are no latent defects in the Goods which would prevent the Goods from being used for their intended purpose or which would impair the utility of the Goods.

  - The deficiencies in Goods/Services and (or) the result of the Services are considered to be non-compliance with the requirements of the Technical Specifications and the legal acts regulating the quality of Goods/Services."

  - The Buyer has the right to contact the Supplier for the correction of deficiencies in the Goods/Services and (or) the result of the Services no later than 10 (ten) working days from the signing of the delivery-acceptance act of the delivered Goods and/or provided Services or the day the deficiencies were recorded.

- TERMS OF PAYMENT

  - The Buyer shall pay to the Supplier for actually delivered Goods and actually provided Service within 30 (thirty) calendar days from the date of receipt of the invoice.

  - The Buyer shall submit a VAT invoice and a signed Goods/Services transfer-acceptance Act to the Buyer within 2 (two) Business Days from the signing of the transfer-acceptance Act for the delivered Goods and/or Services provided.

- DOCUMENTS ACCOMPANYING THE DELIVERED GOODS

  - Certificate of delivery and acceptance of the result of the Goods / Services;

  - Descriptions of Goods in Lithuanian or English;

  - Calibration reports in Lithuanian or English;

  - User and maintenance manuals in Lithuanian or English;