| The Lithuanian Armed Forces Staff Service of the Logistics Board Email: Raimondas.Marozas@mil.lt | 2024-08- No. 2024/S.4-5/5.E- In response to the request received on 13/08/2024 |
| --- | --- |

CONNECTION CONDITIONS

For water supply and wastewater disposal in Klaipėda city and Klaipėda district.

Object name and address: Water supply and wastewater networks for Special Purpose Buildings (plot cad. No. 5552/0001:37, plot cad. No. 5552/0001:557) Klaipėda district municipality, Priekulė eldership, Kairiai village, construction project.

Client - Ministry of National Defence of the Republic of Lithuania

Developer - Klaipėda District Municipality Administration.

Developer - Klaipėda City Municipality Administration.

General instructions:

When designing water supply and wastewater networks, follow the special plan approved by the Klaipėda District Municipality Council decision No. T11-279 of 25/08/2022 “On the approval of the amendment to the special plan for the development of drinking water supply and wastewater management infrastructure in Klaipėda district.”

When designing water supply and domestic wastewater networks, consider the solutions outlined in the technical work project “Water supply and wastewater networks of local significance in the road (No. LM0901), Klaipėda city and local significance road (No. KL1278), and Draustinio St., Kairiai village, Klaipėda district municipality, construction project” prepared by UAB “Green Energy Studio” in 2020. Additionally, evaluate the potential future water and domestic wastewater volumes.

When designing water supply and domestic wastewater networks, consider the solutions of the technical project “Reconstruction and construction project of water supply and wastewater networks in Klaipėda city municipality, Kairiu St.” prepared by UAB “Sweco Lietuva” in 2023.

According to the decision of the Director of Klaipėda City Municipality Administration No. AD1-4 of 2013-01-02 “On the approval of the special plan for the sanitary protection zone of the third water intake of Klaipėda city,” the third water intake belongs to the Illb2 group of infiltration-type water intakes. The planned territory falls within the third sanitary protection (chemical pollution restriction) zone of the third water intake, where restrictions specified in Article 106, Part 9 of the Law on Special Land Use Conditions of the Republic of Lithuania apply.

We inform you that there are no centralized networks available on your plot. To connect to the centralized networks, it is necessary to lay shared-use networks. According to the “Law on the Development of Municipal Infrastructure of the Republic of Lithuania,” when laying shared-use networks, a municipal infrastructure development agreement must be concluded. After signing the agreement, a construction project for the shared-use engineering network must be prepared, with the developers being Klaipėda District Municipality and Klaipėda City Municipality.

For drinking water supply, the developer (client) must:

The nearest centralized water supply networks suitable for connection are approximately 3,000 m from the plot, unique boundary (No. 5552/0001:557), Kairiu St., Klaipėda city.

Design shared-use water supply networks with the appropriate calculated diameter, connecting to the shared-use water supply networks owned by AB “Klaipėdos vanduo,” located in Kairiai St., Klaipėda city, water well No. 106 (143) (PL 24/54-0290) (coordinates x=6171355, y=322254).

Select the network diameter considering projected water consumption.

Install shut-off valves with rubber vulcanized gates at the connection point or well at the planned intersection of the shared-use water supply networks.

To prevent road surface damage, install branches up to the boundary of the plot(s) to be connected, with shut-off valves, positioned at least 1 meter from the outer boundaries of the plot(s). Ensure compliance with drinking and fire water supply requirements.

For domestic wastewater disposal, the developer (client) must:

The nearest centralized pressure domestic wastewater networks are approximately 3,650 m from the plot boundary (unique No. 5552/0001:557), near Taikos Ave. 164, Klaipėda city.

Design shared-use domestic wastewater networks of the appropriate calculated diameter, connecting to the pressure domestic wastewater networks near Taikos Ave. 164, Klaipėda city, chamber No. 152 (143) (PL 24/54-0272) (coordinates x=6171590, y=322772).

Install branches up to the boundary of the plot(s) to be connected to avoid road surface damage.

Maintain the maximum depth of wastewater networks to ensure connectivity for future plots.

Select the diameter of the domestic wastewater networks considering projected wastewater volumes

Use hermetically sealed ductile iron well covers with rubber gaskets for wells. To reduce the entry of excess water (surface, groundwater, etc.) into the domestic wastewater networks, design and install plastic wells.

Ensure that surface runoff and drainage water are not discharged into the domestic wastewater networks.

Additional requirements:

Design shared-use networks in designated public-use areas. If the designed shared-use networks fall into formed plots, a servitude for the use and maintenance of the shared-use networks must be planned in the protection zone area of the designed shared-use networks (servitude code 222). The servitude must be clearly marked in the prepared project. Submit the written consent of the plot owner for the construction of networks and/or the establishment of a servitude in the plot as part of the project.

Before signing the infrastructure development agreement, the company must submit the project solutions for review. For the conclusion of the agreement, provide the scheme of the shared-use networks upon separate request.

When designing shared-use networks, evaluate the possibility of extending the networks and connecting other plots' networks. Design shared-use networks in streets and public-use areas.

The developer will be allowed to use the water supply and wastewater disposal systems only after implementing the shared-use water supply and wastewater network project and handing over the networks and equipment necessary for the connection of the plot networks for operation. For the connection of networks to the street networks, it will be necessary to follow the actual heights of the completed street networks and, if necessary, adjust the coordinates and altitudes of the connection points.

If the constructed networks are closer to property boundaries than allowed by regulations, obtain written consent from affected landowners and submit it as part of the construction project.

Lay the networks in the territory belonging to the client and public-use area. When laying networks in the territory belonging to the co-owner or third parties of the plot, submit the written consent of the plot co-owner/owner.

Maintain the requirements of the network protection zones and the normative depths of the networks established by the applicable legal acts.

When installing wells in water-bearing soil, follow the requirements of STR 2.07.01:2003 p.320.6. and p.417.4.

Well covers in roadway areas must cast iron, floating type, with a long-lasting gaskets, and highly impermeable to surface water, with automatic fixation. In exceptional cases, concrete-filled alternatives may be designed with wastewater network operator approval, which would be no worse than the parameters specified in the standards of AB “Klaipėdos vanduo”. Well covers installed in the non-driving part of the road must be made of cast iron, composite material, or equivalent.

Provide surface runoff disposal solutions in the project.

When performing design and construction works, follow normative construction technical documents, design networks from pipes, fittings, and shaped parts according to the company's approved standards.

If designing a shared-use wastewater pumping station for transfer to Klaipėda city or district municipality and/or AB “Klaipėdos vanduo” after the construction of the networks, it must be designed according to the company's standards “Wastewater network infrastructure standard”, “Requirements for automation of small NPS. Communication type – GPRS”, “Requirements for automation of limited user number wastewater collection pumping station (NSS). Communication type – GPRS”.

All applicable company standards are available at: https://www.vanduo.lt/standartai/.

Obtain approval from AB “Klaipėdos vanduo” for the project in the established manner:

- If the project will be coordinated in the information system “Infostatyba”, to ensure smooth and quick coordination of the project solutions, we suggest submitting the digital version of the project (in pdf format) to the company and obtaining the company's approval before uploading the project to the information system “Infostatyba”.

- If the project will not be coordinated through the information system “Infostatyba”, submit the digital version of the project (in pdf format) to the company and obtain the company's approval.

When handing over the project, submit engineering network plans in digital format to AB “Klaipėdos vanduo”. Ensure all infrastructure elements are documented, including wells, chambers, and underground valves under 1000 mm in diameter.

Conduct cadastral measurements of the constructed shared-use water supply and wastewater networks and legalize their ownership.

When connecting to the wastewater networks operated by AB “Klaipėdos vanduo”, it is mandatory to apply in writing to the company according to the “Procedure for connecting new clients to the water supply and/or wastewater networks of AB “Klaipėdos vanduo” (for more details follow the link https://www.vanduo.lt/prisijungimo-prie-tinklu-tvarka/  Stage IV: Connection to centralized networks). If the company is not notified, the connection will be considered unauthorized, for which fines are imposed.

If the design of engineering networks starts after a 3-month period from the date of issuance of these connection conditions, we recommend contacting the company for clarification if the situation around the address specified in the connection conditions has not changed. Please submit the inquiry by email to technika@vanduo.lt, indicating the object address and the registration number of the connection conditions.

Using water supply and wastewater management services without a contract is prohibited.

Visual information on existing networks is available at: https://wtg.vanduo.lt/IMS/lt.

Head of Infrastructure Construction Department 		Matas Grikšas

Coordinated by:

Head of Technical Documentation and Project Coordination 	Tautvydas Paliulis

Head of Network Maintenance Service 			Marius Martynaitis

Conditions prepared by: Lina Makūnienė, tel. +370 46 220 220, email: lina.makuniene@vanduo.lt