| Lithuanian Armed Forces Staff Service of the Logistics Board Email: Raimondas.Marozas@mil.lt | 2024-09-01 No. 2024/S.4-5/5.E- In response to the request received on 13/08/2024 |
| --- | --- |

CONNECTION CONDITIONS

For water supply and wastewater disposal in Klaipėda district.

Object name and address: Water supply and wastewater networks for Special Purpose Buildings (plot cad. No. 5552/0001:37, plot cad. No. 5552/0001:557) Klaipėda district municipality, Priekulė eldership, Kairiai village, construction project.

Client - Ministry of National Defence of the Republic of Lithuania.

General instructions:

When designing water supply and wastewater networks, follow the special plan approved by the Klaipėda District Municipality Council decision No. T11-279 of 2022-08-25 “On the approval of the amendment to the special plan for the development of drinking water supply and wastewater management infrastructure in Klaipėda district.”

According to the decision of the Director of Klaipėda City Municipality Administration No. AD1-4 of 2013-01-02 “On the approval of the special plan for the sanitary protection zone of the third water intake of Klaipėda city”, the third water intake of Klaipėda city belongs to the Illb2 group of infiltration-type water intakes. The planned territory falls into the third sanitary protection (chemical pollution restriction) zone of the third water intake of Klaipėda city, where the restrictions specified in Article 106, Part 9 of the Law on Special Land Use Conditions of the Republic of Lithuania apply. In this zone, the construction and operation of objects are permitted only by connecting to centralized domestic wastewater networks or local wastewater disposal networks that ensure an equivalent level of environmental protection as municipal wastewater disposal networks, in compliance with legal requirements.

For drinking water supply, the client must:

The connection of the water supply inlet is possible through one of the following options:

- Design the connection of the water supply inlet to the shared-use water supply networks designed according to the connection conditions issued by AB “Klaipėdos vanduo” for the object “Water supply and wastewater networks for Special Purpose Buildings (plot cad. No. 5552/0001:37, plot cad. No. 5552/0001:557) Klaipėda district municipality, Priekulė eldership, Kairiai village, construction project” (2024-08-30 reg. No. 2024/S.4-5/5.E-1066), towards the boundary of the plot, unique No. 5552/0001:557.

- If shared-use centralized water supply networks are not laid, temporarily provide drinking water supply through local solutions, following the requirements of applicable legal acts and normative documents. 
The connection to centralized water supply networks must be made when they become available..

To disconnect the inlet, install European-type shut-off valves in the public-use area, ensuring they are no closer than one meter from the outer boundary of the plot.

The water metering unit should be planned in a specially designated, easily accessible room near the outer wall of the water supply system, ensuring an air temperature of no less than +5°. A check valve must be installed in the water metering unit to prevent backflow from the building's internal water supply networks. If it is not possible to install the water metering unit indoors, it must be installed in a dedicated metering well, complying with all installation requirements. The well should be placed in an easily accessible shared-use area, ensuring unrestricted access at all times. The water metering unit must comply with the requirements of STR 2.07.01:2003.

For domestic wastewater disposal, the client must:

The connection of the domestic wastewater outlet is possible through one of the following options:

- Design the connection of the domestic wastewater outlet to the shared-use domestic wastewater networks designed according to the above-mentioned connection conditions.

- If shared-use centralized domestic wastewater networks are not laid, temporarily provide domestic wastewater disposal through local solutions, ensuring an equivalent level of environmental protection as municipal wastewater disposal networks, in compliance with legal requirements and applicable normative documents. 
The connection to centralized domestic wastewater networks must be made when they become available.

The concentration of pollutants in the discharged domestic wastewater must not exceed the values specified in the Wastewater Management Regulation (approved by the order of the Minister of Environment of the Republic of Lithuania No. D1-236 of 2006-05-17 with subsequent amendments).

In case of pollution, install a control well for wastewater sampling in the public-use area.

To minimize excess water (surface, groundwater, etc.) entering the domestic wastewater networks, design and install plastic wells.

Use hermetic, ductile iron well covers with rubber gaskets for wells.

Surface runoff and drainage water must not be discharged into the domestic wastewater networks.

Additional requirements:

The client will be allowed to use the water supply and wastewater disposal systems according to the above-mentioned connection conditions only after preparing and implementing the shared-use network project and handing over the networks and necessary equipment for the connection of plot networks for operation. The connection of networks to the street networks must follow the actual heights of the completed street networks adjusting the coordinates and altitudes of the connection points if necessary.

Lay the networks within the client’s territory and public-use area. When laying networks in the territory of a co-owner or third parties, submit written consent from the plot co-owner/owner.

Submit surface runoff disposal solutions as part of the project.

Maintain the requirements of network protection zones and the normative depths established by applicable legal acts.

When installing wells in water-bearing soil, follow the requirements of STR 2.07.01:2003 p.320.6. and p.417.4.

Perform design and construction works in compliance with normative construction technical documents, using pipes, fittings, and shaped parts according to the company's approved standards.

All relevant company standards are available at: https://www.vanduo.lt/standartai/.

Obtain the approval of AB “Klaipėdos vanduo” for the project in the established procedure:

- If the project will be coordinated in the information system “Infostatyba,” to ensure smooth and quick coordination of the project solutions, we suggest submitting the digital version of the project (in pdf format) to the company and obtaining the company's approval before uploading the project to the information system “Infostatyba.”

- If the project will not be coordinated through the information system “Infostatyba,” submit the digital version of the project (in pdf format) to the company and obtain the company's approval.

Upon project completion, submit the constructed engineering network plans and one digital copy of the engineering network plan to AB “Klaipėdos vanduo.” The plan must include all wells/chambers and underground valves with a diameter or dimensions smaller than 1000 mm, along with their records.

When connecting to wastewater networks operated by AB “Klaipėdos vanduo,” submit a written application according to the "Procedure for connecting new clients to the water supply and/or wastewater networks of AB “Klaipėdos vanduo” (more details following the link https://www.vanduo.lt/prisijungimo-prie-tinklu-tvarka/ Stage IV: Connection to centralized networks). If the company is not notified, the connection will be considered unauthorized, for which fines are imposed.

If the design of engineering networks starts after a 3-month period from the date of issuance of these connection conditions, we recommend contacting the company for clarification if the situation around the address specified in the connection conditions has not changed. Please submit the inquiry by email to technika@vanduo.lt, indicating the object address and the registration number of the connection conditions.

Using water supply and wastewater management services without a contract is prohibited.

Visual information on existing networks is available at: https://wtg.vanduo.lt/IMS/lt.

Head of Infrastructure Construction Department 		Matas Grikšas

Coordinated by:

Head of Technical Documentation and Project Coordination 	Tautvydas Paliulis

Conditions prepared by: Lina Makūnienė, tel. +370 46 220 220, email: lina.makuniene@vanduo.lt