## 1. Creation of buildings. Needs
Supplement 2.1 document 10 "Technical requirements for the creation of a sports complex"
| Project name |  | Development of a military campus infrastructure in Klaipėda district, Kairiai
| Facility |  | Kairiai military town
| Type of construction |  | New construction
| Annex to terms & conditions |  | Annex 2 Specifications
| Supplement |  | Supplement 2.1 document 10 "Technical requirements for the creation of a sports complex"
| Supplement document (worksheet) |  | worksheet 1. Needs
Item No. | The name of the room/space/functional block | Number of places | Phones connected to the KATT | Computer networks are connected to the unit's network 2 | Computer networks are connected to the KAS network 1 | Number of computerised workstations | Approximate area (sq. m) (if needed to determine) | The significance level of the room/space/functional block (A, B, C and D) | Description of special requirements for premises/areas (if applicable) | The area of the premises/space/functional block in square metres proposed by the Candidate/Participant | numbering of premises according to the explanations on the drawings proposed by the Candidate/Participant | Cost of development of the solution proposed by the Candidate / Participant (EUR excl. VAT) | Furniture/equipment inventory |  |  |  | Possible optimisation proposed by the Candidate – additional solutions to those in the Specification (reference to the Tender document, section, paragraph, clause). Price (EUR excl. VAT) This section is to be completed only for the Initial Tender | REMARKS
[13 empty] | Description of the building's furniture/equipment inventory needs and Special Requirements (if any) | The planned furniture/equipment inventory is purchased by *PS, **PS, or VS | The price of furniture and equipment proposed by the Candidate/Participant for the investor (which is purchased by the Private Entity) (*PS, **PS)) (EUR excl. VAT) | Cost for the installation of the furniture and equipment inventory proposed by the Candidate/Participant (*PS, **PS) (EUR excl. VAT)
| To be completed by the Public entity (PE). When submitting the Tender, the information “To be completed by the Candidate/Participant" may be suspplemented by the Candidate/Participant | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | to be completed by Candidate / Participant | to be completed by Candidate / Participant | to be completed by Candidate / Participant | To be completed by Public entity | To be completed by Public entity | to be completed by Candidate / Participant | to be completed by Candidate / Participant | To be completed by the candidate (only applicable for Initial Tender)
Indoor Sports Complex
1. | Administrative area |  | 6 | 0 | 7 | 7 | 52 |  | *Security systems for the premises are installed in accordance with document 36 of Annex 2.1, "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of access to the building and building entrance, Access control system to the premises – not provided.
1.1. | Physical training specialist's office | 3 | 3 | - | 3 | 3 | 24 | B | The room must include IP television. |  |  |  | Provide spaces for office furniture set No. 3 – 3 unit (according to document 28 of Annex 2 Supplement 2 of the Terms); | *PS
1.2. | Medical staff room | 1 | 1 | - | 2 | 2 | 12 | B | The room must include IP television. There must be direct access to the medical staff room from the administrative zone and from the exterior of the building, with the possibility of access with stretchers and wheelchairs. |  |  |  | Provide spaces for office furniture set No 4. 3 – 1 unit (according to document 29 of Annex 2 Supplement 2 of the Terms); bed – 1 pcs; medication cabinet – 1 unit. | *PS
1.3. | Guard's office | 2 | 2 | - | 2 | 2 | 16 | A | The room must include IP television. At the guard's office, provide turnstiles for access to the sports complex (2 units with card readers and integrated into the access control system), and provide additional turnstile control via a button from the guard's office. In the common building areas, provide space for table tennis (the tennis tables will be purchased by the Public Entity). |  |  |  | Provide spaces for office furniture set No. 3 – 1 unit (according to document 29 of Annex 2 Supplement 2 of the Terms); | *PS
3. | Sports hall area | [7 empty] | *Magnetic contacts for security alarm systems are planned for the movable parts of the building’s exterior windows and doors and are assigned to the corridor area.
3.1. | Universal sports hall (basketball, volleyball, outdoor tennis, badminton) | 1 | - | - | 1 | 1 | 680 | C | The universal sports hall must be adapted for the following sports: Basketball, handball, volleyball, outdoor tennis, and badminton competitions. The hall surface – wooden. Mark the courts according to the applicable standards, considering the hall's use for the following: Basketball, handball, volleyball, outdoor tennis, and badminton competitions. The height of the universal sports hall must be no less than 9 m, with retractable protective nets and window protection at the ends of the hall. The additional equipment storage room must be adjacent to the hall and have direct access to it. Install easily removable or detachable floor protection for the sports hall during non-sporting events and provide space for storing the floor protection. Install lighting equipment and sound system. The hall must be capable of installing 4 training (basketball) courts, with a net system for separating them. The structure, marking, equipment, and flooring of the sports halls in the premises must be adapted for different types of sporting activities. The premises must be adapted to organize sporting events for people with disabilities. |  |  |  | Provide mobile, foldable spectator stands – 100 seats, electronic scoreboard 1 set sound system – 1 set, mobile basketball stands – 2 pcs indoor soccer goals 2 pcs. volleyball stands with a net – 2 pcs; universal umpire tower with a scoreboard for volleyball and/or outdoor tennis courts – 1 set (according to document 31 of Supplement 2 of Annex 2.1 of the Terms) | *PS
3.2. | Military combat self-defense hall | 1 | - | - | 1 | 1 | 160 | C | Install a 12x12 m mat area (competition regulation-compliant tatami) in this zone. Install fastenings (2 rows, 3 m gap between the rows, 5 fastenings in each row, 3 m apart from each other) with a lifting capacity of at least 150 kg (for boxing bags).On one of the walls (across the entire length of the wall), install mirrors at least 1.8 m high, raised 0.5 m from the floor. In the area designated for combat wrestling and special techniques training, the surface must be of "tatami" type, at least 4 cm thick, uniform in colour, with the necessary walkways around the surface. Secure the mat (sporting surface) with edging to prevent any gaps between them. A 1.5-1.2 m passage around the mat is required. If it is not possible to create a passage at any wall, the wall must be covered with soft material. Prepare inventory layout plans, diagrams. |  |  |  | The room must include a Swedish wall. – 5 pcs; boxing bags – 8 pcs; suspended boxing speed balls – 4 units. (according to document 31 of Supplement 2 of Annex 2.1 of the Terms) | *PS
3.3. | Gym / Functional sports and group exercise room | 1 | - | - | 1 | 1 | 380 | C | Install rubber flooring suitable for gym areas. On two walls (across the entire length of the wall), hang mirrors at least 2 m high (raised 0.5 m from the floor). The room must include IP television. Prepare inventory layout plans, diagrams. |  |  |  | Provide gym equipment for various muscle groups. – 30 units. Wooden gymnastics walls with removable bars for pull-ups – 5 units. (according to document 31 of Supplement 2 of Annex 2.1 of the Terms) | *PS
3.4. | Sauna | 1 | - | - | - | - | 20 | C | Provide all equipment and furniture required for the room's functionality.
3.5. | Changing rooms with showers (including referee's locker room, 5 seats, with shower and WC facilities) | 1 | - | - | - | - | 80 | C | The changing rooms must be connected to the shower and toilet facilities. The changing rooms and sanitary facilities must be easily accessible from the exterior and interior rooms with sports equipment, and adapted for children and people with disabilities. Sanitary rooms must be of adequate size and carefully planned in all public areas. Access to the sauna must be provided from the changing rooms. |  |  |  | Provide lockable changing lockers – 50 units. Wooden benches – 20 units. (according to document 31 of Supplement 2 of Annex 2.1 of the Terms) | *PS
4. | Sports hall area |  | 0 | 0 | 1 | 1 |  |  | *Magnetic contacts for security alarm systems are planned for the movable parts of the building’s exterior windows and doors and are assigned to the corridor area.
4.1. | Gym | - | - | - | 1 | 1 | 280 | C | Install rubber flooring suitable for gym areas on one of the walls (across the entire length of the wall), hang mirrors at least 2 m high (raised 0.5 m from the floor). The room must include IP television. Prepare inventory layout plans, diagrams. |  |  |  | Provide gym equipment for various muscle groups. – 30 pcs; wooden gymnastics walls with removable bars for pull-ups – 5 units. mattress – 5 units. (according to document 31 of Supplement 2 of Annex 2.1 of the Terms) | *PS
4.2. | Sauna | 20 | - | - | - | - | 20 | C |  |  |  |  | Provide all equipment and furniture required for the room's functionality. | *PS
4.3. | Functional sports and group exercise room | 5 | - | - | - | - | 120 | C | On one of the walls (across the entire length of the wall), hang mirrors at least 2 m high (raised 0.5 m from the floor). |  |  |  |  | *PS
4.4. | Changing rooms with showers (including referee's locker room, 5 seats, with shower and WC facilities) | 6 | - | - | - | - | 80 | C | The changing rooms must be connected to the shower and toilet facilities. The changing rooms and sanitary facilities must be easily accessible from the exterior and interior rooms with sports equipment, and adapted for children and people with disabilities. Sanitary rooms must be of adequate size and carefully planned in all public areas. Access to the sauna must be provided from the changing rooms. |  |  |  | Provide lockable changing locker – 50 pcs; Wooden benches – 20 units. (according to document 31 of Supplement 2 of Annex 2.1 of the Terms) | *PS
5. | Storage facilities | [7 empty] | *Security systems for the premises are installed in accordance with document 36 of Annex 2.1, "Requirements for the installation of electronic security systems" Type 1 room, Video surveillance – general monitoring of access to the building and building entrance, Access control system – not provided.
5.1. | Sports equipment storage zone | 1 | - | - | 1 | 1 | 25 | C | The sports equipment storage room(s) must be designed and installed so that access to all sports zones is possible from there. |  |  |  | Provide racks (according to document 26 of Annex 2 Supplement 2.1 of the Terms) (4 units). | *PS
5.2. | Sports equipment storage zone | 1 | - | - | 1 | 1 | 12 | C | The sports equipment storage room(s) must be designed and installed so that access to all sports zones is possible from there. |  |  |  | Provide racks (according to document 26 of Annex 2 Supplement 2.1 of the Terms) (4 units). Provide spaces for office furniture set No. 3 – 1 unit (according to document 29 of Annex 2 Supplement 2 of the Terms); | *PS
5.2. | Sports equipment repair room (can be within the general storage zone) | 1 | - | - | 1 | 1 | 20 | C |  |  |  |  | Provide racks (according to document 26 of Annex 2 Supplement 2.1 of the Terms) (4 units). | *PS
6. | Storage facilities |  | 0 | 0 | 2 | 2 | 37 |  | *Security systems for the premises are installed in accordance with document 36 of Annex 2.1, "Requirements for the installation of electronic security systems" Type 1 room, Video surveillance – general monitoring of access to the building and building entrance, Access control system to the premises – not provided.
6.1. | Sports equipment storage zone | 1 | - | - | 1 | 1 | 25 | C | The sports equipment storage room(s) must be designed and installed so that access to all sports zones is possible from there. |  |  |  | Provide racks (according to document 26 of Annex 2 Supplement 2.1 of the Terms) (4 units). | *PS
6.2. | Sports equipment storage zone | 1 | - | - | 1 | 1 | 12 | C | The sports equipment storage room(s) must be designed and installed so that access to all sports zones is possible from there. |  |  |  | Provide racks (according to document 26 of Annex 2 Supplement 2.1 of the Terms) (4 units). Provide spaces for office furniture set No. 3 – 1 unit (according to document 29 of Annex 2 Supplement 2 of the Terms); | *PS
7. | Special-purpose rooms | [7 empty] | *Security systems for the premises are installed in accordance with document 36 of Annex 2.1, "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of access to the building and building entrance, Access control system to the premises – not provided.
7.1. | Laser shooting range | 10 | 1 | - | - | 10 | 130 | C | Provide space and necessary connections for the equipment. Equipment will be purchased by the Public Entity. |  |  |  |  | PE
7.2. | Inventory storage room | - | - | - | - | - | 20 | C |  |  |  |  | Provide racks (according to document 26 of Annex 2 Supplement 2.1 of the Terms) (4 units). | *PS
7.3. | Instructors' office | 3 | 3 | - | 3 | 3 | 18 | C |  |  |  |  | Provide spaces for office furniture set No. 3 – 1 unit (according to document 29 of Annex 2 Supplement 2 of the Terms); | *PS
7.4. | Instructors' office | 3 | 3 | - | 3 | 3 | 18 | C |  |  |  |  | Provide spaces for office furniture set No. 3 – 1 unit (according to document 29 of Annex 2 Supplement 2 of the Terms); | *PS
7.5. | Methodical classroom | 30 | 1 | - | 3 | 3 | 50 | C |  |  |  |  | Provide a set of auditorium furniture No. 9 – 1 pcs. (according to document 29 of Annex 2 Supplement 2 of the Terms); | *PS
7.6. | Methodical classroom | 30 | 1 | - | 3 | 3 | 50 | C |  |  |  |  | Provide a set of auditorium furniture No. 9 – 1 pcs. (according to document 29 of Annex 2 Supplement 2 of the Terms); | *PS
8. | Common use rooms |  | 0 | 0 | 0 | 0 | 130 |  | *Magnetic contacts for security alarm systems are planned for the movable parts of the building’s exterior windows and doors and are assigned to the corridor area.
8.1. | Cleaning inventory room | 1 | - | - | - | - | 10 | C | Each floor of the building must include technical rooms for storing cleaning equipment. Forced air extraction must be ensured in these rooms, with a sink equipped with hot and cold water connections, and holders must be provided for convenient storage of brushes and other tools. |  |  |  | Provide all equipment and furniture required for the room's functionality. | PS
8.2. | WC for visitors / changing room | 1 | - | - | - | - | 120 | C |  |  |  |  | Provide all equipment and furniture required for the room's functionality. | PS
9. | Building engineering system rooms |  | 0 | 0 | 0 | 0 | 40
9.1. | Technical rooms | - | - | - | - | - | 20 | C | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 1 room. Video surveillance – general monitoring of building access points and entrances, Access control system – not planned.
9.2. | Electronic security systems switch room | - | - | - | - | - | 6 | A | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 4 room.
9.3. | Switching room (communication distribution point) | - | - | - | - | - | 14 | A
10. | Other rooms |  | 0 | 0 | 0 | 0 | 642 | 0
10.1. | Corridor | 1 | - | - | - | - | 642 | C | In the corridors, provide space with electrical wiring for the installation of a coffee/snack machine and drinking water equipment. Separate access points from the administrative zone to all sports zones must be provided. Direct access from the administrative zone to the physical training specialists' office must be provided.
11. | Other. Proposed by the Candidate / Participant. | [7 empty] | The Candidate/Participant may supplement their Tender with the solutions that do not contradict the Specifications or are not assessed by the Public Entity (PE)
Total building area
The price must match the price of part of the Facility of Supplement 2.1, document 1, worksheet 1
[12 empty] | Total (EUR, excl. VAT) |  |  |  |  | Total cost of the optimisation solutions (EUR excl. VAT). Cost of additional work or savings
REMARKS:
1. The Public Entity fills in the specifications, object data, and design task taking into account the features and purpose of the object.
2. The Public Entity provides known special requirements and descriptions of objects, rooms, spaces, functional blocks, and infrastructure. If descriptions are not provided in the Public Entity tables, the Candidate/Participant must submit their tenders in accordance with applicable regulations, standards, and other legal acts.
3. The Candidate/Participant may propose and suggest possible optimisations in their solutions (by suggesting to supplement the Specifications, justifying the benefits of the proposals and their impact on the price of the Tender).
4. The Public Entity classifies rooms/ spaces/ functional blocks by significance levels into functional sector significance levels A, B, C, and D (Specifications section "Functional sectors").
5. The areas provided in the table are approximate and may change depending on the implementation of regulatory acts and the requirements of the Specifications.
6. The technological rooms must be equipped with an air conditioning system, ensuring the proper operating conditions for the equipment installed in these rooms. Parameters are selected according to the recommendations of computer network equipment manufacturers. Temperature deviations in the rooms must be automatically recorded in the Registration Tool.
7. The size of technological premises indicated in the table is approximate, it is adjusted by evaluating the planned equipment quantities to be installed. The size of the room must allow easy access to the switchgear cabinets and equipment maintenance.
10. Technological rooms should not be located beneath sanitary facilities or in other areas where there is a high risk of flooding.
11. If necessary to clarify the solutions, the Participant may add rows to their table.
12. * The PS must provide for a one-time furniture purchase and warranty maintenance for a period of 5 years
13 The PS must provide equipment/furniture that is mandatory (or necessary) for the proper functioning (use) of buildings/premises, in accordance with legal acts/regulations, the Private Entity’s solutions, etc., including their further technical maintenance throughout the entire Contract period
14. VS – Furniture and equipment purchased and installed by the PUBLIC ENTITY.

## 2. Creation of buildings. Needs
Supplement 2.1 document 10 "Technical requirements for the creation of a sports complex"
| Project name |  | Development of a military campus infrastructure in Klaipėda district, Kairiai
| Facility |  | Kairiai military town
| Type of construction |  | New construction
| Annex to terms & conditions |  | Annex 2 Specifications
| Supplement |  | Supplement 2.1 document 10 "Technical requirements for the creation of a sports complex"
| Supplement document (worksheet) |  | worksheet 2. Needs
Item No. | The name of the room/space/functional block | Number of places | Phones connected to the KATT | Computer networks are connected to the unit's network 2 | Computer networks are connected to the KAS network 1 | Number of computerised workstations | Approximate area (sq. m) (if needed to determine) | The significance level of the room/space/functional block (A, B, C and D) | Description of special requirements for premises/areas (if applicable) | The area of the premises/space/functional block in square metres proposed by the Candidate/Participant | numbering of premises according to the explanations on the drawings proposed by the Candidate/Participant | Description of solutions proposed by the Candidate/Participant (reference to the annex of the Tender: Section, part, item of the Tender | Cost of development of the solution proposed by the Candidate / Participant (EUR excl. VAT) | Furniture/equipment inventory |  |  |  | Possible optimisation proposed by the Candidate – additional solutions to those in the Specification (reference to the Tender document, section, paragraph, clause). Price (EUR excl. VAT) This section is to be completed only for the Initial Tender | REMARKS
[14 empty] | Description of the building's furniture/equipment inventory needs and Special Requirements (if any) | The planned furniture/equipment inventory is purchased by *PS, **PS, or VS | The price of furniture and equipment proposed by the Candidate/Participant for the investor (which is purchased by the Private Entity) (*PS, **PS)) (EUR excl. VAT) | Cost for the installation of the furniture and equipment inventory proposed by the Candidate/Participant (*PS, **PS) (EUR excl. VAT)
| To be completed by the Public entity (PE). When submitting the Tender, the information “To be completed by the Candidate/Participant" may be suspplemented by the Candidate/Participant | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | to be completed by Candidate / Participant | to be completed by Candidate / Participant | to be completed by Candidate / Participant | to be completed by Candidate / Participant | To be completed by Public entity | To be completed by Public entity | to be completed by Candidate / Participant | to be completed by Candidate / Participant | To be completed by the candidate (only applicable for Initial Tender)
1. | Outdoor sports complex (2 pcs) |  | 0 | 0 | 0 | 0 | 2083
1.1. | Multipurpose sports field (45X30 m) | 1 | - | - | - | - | 1350 | B | The sports grounds consist of playing fields for handball (1 unit), outdoor tennis, basketball, volleyball, and badminton (2 units of each). |  |  |  |  | Provide equipment suitable for outdoor conditions: handball goals with nets – 1 set, outdoor tennis posts with nets – 2 set, volleyball posts with nets – 2 set, basketball posts with protective barriers (to prevent injuries), backboards, hoops, and nets – 4 set Provide mobile spectator stands (100 people); Provide mobile outdoor benches with supports (15 seats) – 4 pcs; | *PS
1.2. | Beach volleyball court. (16x8 m) | 1 | - | - | - | - | 128 | C | [5 empty] | Provide posts with nets – 1 set, court marking tapes – 1 set, universal referee stand for refereeing with a results scoreboard – 1 set, mobile outdoor benches with supports (4 seats) – 2 units. Install mobile outdoor benches with supports (4 seats) 2 pcs. Provide a universal referee stand for refereeing with a results scoreboard – 1 set | *PS
1.3. | Outdoor equipment and sports zone (10x10 m) | 2 | - | - | - | - | 200 | C | The outdoor equipment complex consists of: horizontal ladders; high horizontal bars; flexion board; platforms; wall-mounted ladder; low horizontal bars (for pull-ups); low horizontal bars (for push-ups); sit-up board; parallel bars. Each horizontal and vertical bar must withstand a load of 150 kg acting vertically from top to bottom. The structure must be fixed, immobile, welded together, coated with anti-corrosion paint resistant to environmental impact, and the horizontal bars must have a non-slip surface. Platforms must be immobile and withstand a load of 150 kg acting vertically from top to bottom. The flexion bench (wooden) should be resistant to environmental impact and should have a strap (attached to the underside of the bench, synthetic, resistant to environmental impact) for securing the feet; the sit-up bench should have rounded corners and be resistant to environmental impact. The area on which the outdoor equipment will stand must be levelled, with a gravel foundation (no less than 10 mm fraction). Install a metal structure to protect from rain, holding logs at a height of 1.5 m. |  |  |  |  | Provide jute bags filled with sand – 8 pcs; TRX straps – 4 pcs; logs (length – 1,5 m, diameter – 0,2 m) – 4 units. Provide all equipment required for the room's functionality. | *PS
Example of typical sports equipment village setup
1.4. | Military self-defence area 15x27 m | 1 | - | - | - | - | 405 | C | Install a soft surface in the centre of the area 9x21 m. The soft surface – made of sand, mulch, or shredded rubber, with a levelled base, edges surrounded by sand-filled bags, intended for acrobatic actions, self-protection in falls, and combat execution. Mannequins should be arranged around the soft surface – 7 units. and holders for large boxing bags – 7 units. with safety zones 3x3 m. The private entity must install – 7 mannequins (steel construction mounted on a solid base, simulating human silhouette contours, covered with durable rubber, capable of withstanding mechanical impacts from several people (360 degrees), intended for executing striking techniques – hands, feet, weapon imitations, and sticks) and 10 boxing bag holders (steel construction mounted on a solid base, capable of withstanding a large suspended boxing bag) |  |  |  |  | a metal box/cabinet with a lock for storing equipment and inventory boxing bag holders 7 pcs.; large boxing bags 7 pcs.; | *PS
1.5. | Other. Proposed by the Candidate / Participant. | [7 empty] | The Candidate/Participant may supplement their Tender with the solutions that do not contradict the Specifications or are not assessed by the Public Entity (PE)
Total building area
The price must match the price of part of the Facility of Supplement 2.1, document 1, worksheet 1
[13 empty] | Total (EUR, excl. VAT) |  |  |  |  | Total cost of the optimisation solutions (EUR excl. VAT). Cost of additional work or savings
1. | Stadium |  | 0 | 0 | 0 | 0
1.1. | Football pitch | - | - | - | - | - | 12500 | B | Design the football pitch, dimensions no less than 105 x 68 m. Install with line markings, corner and centre markings – flags. |  |  |  |  | Provide equipment suitable for outdoor conditions: stationary football goals (7,32 x 2,44 m) with nets – 2 pcs; portable football goals (7,32 x 2,44 m) with nets – 2 pcs; portable football goals (5 x 2 m) with nets – 4 pcs; electronic scoreboard – 1 set, surface maintenance equipment – 1 set, non-sharp corner flag – 4 units. | *PS
1.2. | Segment A | - | - | - | - | - |  | B | Provide an open space/green lawn.
1.3. | Segment B | - | - | - | - | - |  | B | Provide an open space/green lawn.
1.4. | Running tracks | - | - | - | - | - |  | B | Provide the installation and marking of running tracks around the football pitch – 4 units. Provide an appropriate running track surface for use in all seasons. Covering material according to its intended purpose (the cover must dry quickly after rain (minimal absorbency), and be resistant to unstable and variable climatic conditions).
1.5. | Stands | - | - | - | - | - | - | B | [5 empty] | Provide spectator stands – no fewer than 510 seats. Provide canopies (for protection from precipitation and sun) for players with chairs (2 units). Provide a canopy for referees ( 1 unit). Provide flagpoles – 5 units. | *PS
1.5. | Other. Proposed by the Candidate / Participant. | [7 empty] | The Candidate/Participant may supplement their Tender with the solutions that do not contradict the Specifications or are not assessed by the Public Entity (PE)
14100
The price must match the price of part of the Facility of Supplement 2.1, document 1, worksheet 1
[13 empty] | Total (EUR, excl. VAT) |  |  |  |  | Total cost of the optimisation solutions (EUR excl. VAT). Cost of additional work or savings
REMARKS:
1. The Public Entity fills in the specifications, object data, and design task taking into account the features and purpose of the object.
2. The Public Entity provides known special requirements and descriptions of objects, rooms, spaces, functional blocks, and infrastructure. If descriptions are not provided in the Public Entity tables, the Candidate/Participant must submit their tenders in accordance with applicable regulations, standards, and other legal acts.
3. The Candidate/Participant may propose and suggest possible optimisations in their solutions (by suggesting to supplement the Specifications, justifying the benefits of the proposals and their impact on the price of the Tender).
4. The Public Entity classifies rooms/ spaces/ functional blocks by significance levels into functional sector significance levels A, B, C, and D (Specifications section "Functional sectors").
5. The areas provided in the table are approximate and may change depending on the implementation of regulatory acts and the requirements of the Specifications.
6. The technological rooms must be equipped with an air conditioning system, ensuring the proper operating conditions for the equipment installed in these rooms. Parameters are selected according to the recommendations of computer network equipment manufacturers. Temperature deviations in the rooms must be automatically recorded in the Registration Tool.
7. The size of technological premises indicated in the table is approximate, it is adjusted by evaluating the planned equipment quantities to be installed. The size of the room must allow easy access to the switchgear cabinets and equipment maintenance.
10. Technological rooms should not be located beneath sanitary facilities or in other areas where there is a high risk of flooding.
11. If necessary to clarify the solutions, the Participant may add rows to their table.
12. * The PS must provide for a one-time furniture purchase and warranty maintenance for a period of 5 years
13 The PS must provide equipment/furniture that is mandatory (or necessary) for the proper functioning (use) of buildings/premises, in accordance with legal acts/regulations, the Private Entity’s solutions, etc., including their further technical maintenance throughout the entire Contract period
a

## 3. Development of buildings.
Supplement 2.1 document 10 "Technical requirements for the creation of a sports complex"
| Project name | Development of a military campus infrastructure in Klaipėda district, Kairiai
| Facility | Kairiai military town
| Type of construction | New construction
| Annex to terms & conditions | Annex 2 Specifications
| Supplement | Supplement 2.1 document 10 "Technical requirements for the creation of a sports complex"
| Supplement document (worksheet) | worksheet 3. Development of buildings. Construction
Item No. | Building part/ System/ Area | Description of special requirements for premises/areas (if applicable) | Indoor sports complex
|  |  | Description of solutions proposed by the Candidate/Participant (reference to the annex of the Tender: Section, part, item of the Tender). | Cost of development of the solution proposed by the Candidate / Participant (EUR excl. VAT) | Possible optimisation proposed by the Candidate – additional solutions to those in the Specification (reference to the Tender document, section, paragraph, clause). Price (EUR excl. VAT) This section is to be completed only for the Initial Tender | REMARKS
| To be completed by the Public entity (PE). When submitting the Tender, the information “To be completed by the Candidate/Participant" may be suspplemented by the Candidate/Participant | to be filled by the Public Entity (if specific requirements are known and applied | to be completed by Candidate / Participant | to be completed by Candidate / Participant | To be completed by the candidate (only applicable for Initial Tender)
1. | Building structures and other elements
1.1. | Foundations | Foundations under supporting structures must be designed considering the loads, the nature of the load increase, and the foundation ground properties. The final decision on the type of foundation must be based on the results of engineering geological studies and a cost comparison of different foundation types. The Participant provides information on selected foundation type, including structures, insulation, and finishing materials etc.
1.2. | Plinth installation | Wall covers (by the type of coating) must be compatible with the room purpose, resistant to wet cleaning and, where necessary, to chemicals used for disinfection. The Participant provides information on plinth solutions, finishing materials etc.
1.3. | Load-bearing external walls, structures | The areas designated for soldier movement must be separated from the external building enclosures to protect the building façades and their external elements from accidental damage. If necessary, external wall cladding must be used, ensuring its acoustic properties. Colours and materials must be selected based on resistance to dirt, ease of cleaning, material aging, wear, and simplicity of maintenance. The architecture of the building's facade must be simple (without intricate details). Facades must be easy to maintain and durable, with facade materials offering increased resistance to dirt and damage. Facade materials must be resistant to adverse climatic effects and urban pollution and/or biological materials (moss, mould, insects, rodents, bird droppings) et al). Wall covers (by the type of coating) must be compatible with the room purpose, resistant to wet cleaning and, where necessary, to chemicals used for disinfection. The Participant provides information on external wall solutions, including structures, insulation, and finishing layers etc.
1.4. | Non-load-bearing external walls, structures | The areas designated for soldier movement must be separated from the external building enclosures to protect the building façades and their external elements from accidental damage. If necessary, external wall cladding must be used, ensuring its acoustic properties. Colours and materials must be selected based on resistance to dirt, ease of cleaning, material aging, wear, and simplicity of maintenance. The architecture of the building's facade must be simple (without intricate details). Facades must be easy to maintain and durable, with facade materials offering increased resistance to dirt and damage. Facade materials must be resistant to adverse climatic effects and urban pollution and/or biological materials (moss, mould, insects, rodents, bird droppings) et al). Wall covers (by the type of coating) must be compatible with the room purpose, resistant to wet cleaning and, where necessary, to chemicals used for disinfection. The Participant provides information on external wall solutions, including structures, insulation, and finishing layers etc.
1.5. | Slabs on the ground. | Acoustic noise in shared areas must not exceed 85 dBA, in work offices and meeting rooms – up to 50 dBA, and in sleeping areas – up to 32 dBA. The floors must be designed to withstand their own weight and operational loads, considering the intended purpose of the rooms. Floor coverings must be suitable for their intended use based on the function of the rooms or spaces where they are installed. The participant provides information about the floor slab structure (insulation types, layers) etc.)
1.6. | Floor slabs between levels | Acoustic noise in shared areas must not exceed 85 dBA, in work offices and meeting rooms – up to 50 dBA, and in sleeping areas – up to 32 dBA. In special rooms with a high or medium potential for liquid accumulation, a floor slope must be installed to allow liquids to drain into the sewage system. Floor coverings must be suitable for their intended use based on the function of the rooms or spaces where they are installed. The floors must be designed to withstand their own weight and operational loads, considering the intended purpose of the rooms. The participant provides information about the floor slab structure (insulation types, layers) etc.)
1.7. | Roof | Measures to prevent the formation of icicles must be provided; The roof must be easy to maintain, with maintenance walkways and platforms installed. Access to the roof must be easy but restricted with safety measures to prevent unauthorized individuals from accessing it. Water from the building’s roof must be drained in such a way that it does not damage the building’s structure, roads, sidewalks, adjacent buildings, or harm the environment, and is directed into the underground stormwater drainage system. The participant provides information about the roof structure, insulation types and layers, and finishes. Rainwater collection and drainage system, roof protective railings, walkways, protective grilles, snow-retaining grilles, fire escape ladders etc.
1.8. | Load-bearing internal walls | Wall covers (by the type of coating) must be compatible with the room purpose, resistant to wet cleaning and, where necessary, to chemicals used for disinfection. If there are niches, it is recommended to install sports equipment or radiators, which are covered so that the surfaces are flush with the wall. The Participant provides information on internal wall solutions, including structures, insulation, and finishing layers etc.
1.9. | Non-load-bearing internal walls | Wall covers (by the type of coating) must be compatible with the room purpose, resistant to wet cleaning and, where necessary, to chemicals used for disinfection. If there are niches, it is recommended to install sports equipment or radiators, which are covered so that the surfaces are flush with the wall. The Participant provides information on internal wall solutions, including structures, insulation, and finishing layers etc.
1.10. | Structural elements | The structure of the buildings must be durable enough to withstand the negative effects of rare and potentially dangerous events. The main criterion when choosing building materials is public safety and material durability. These materials must be used in such a way that they meet the requirements or are of better quality than those specified in the technical requirements of these Specifications. The Participant provides information on stairs, ramps, balconies, and loggia structures, including coatings etc.
1.11. | Partitions | The finishing of partitions can be minimal (for example, where allowed by the construction norms, walls can be left unplastered, painted, or impregnated), but must comply with the intended use of the rooms. Wall covers (by the type of coating) must be compatible with the room purpose, resistant to wet cleaning and, where necessary, to chemicals used for disinfection. The Participant provides information on Partition types, structures, finishes etc.
1.12. | Floor coverings and finishes. | Floors must be level, non-slip, crack-free, waterproof, easy to clean with a damp method, and resistant to chemical cleaners and disinfectants. When selecting floor coverings for the universal sports, military self-defence, gym, and administrative areas, comply with the relevant construction technical standards and safety regulations for the building’s intended purpose. The properties of the floor constructions and coverings must ensure the main requirements of the building over the economically justified usage period. The structures of sports halls, including floors, must be durable and safe, allowing for the attachment of stationary or portable equipment. Walls must be flat, without recesses or protrusions. The floors in the area where the carpet will be laid must be wooden. Walls and ceilings must be covered with a smooth, durable, and moisture-resistant material. Install rubber flooring suitable for gym areas. The Participant provides information on floor type, structures, finish. The main room groups are distinguished – corridors, halls, administrative rooms, service rooms, and technical auxiliary rooms etc.
1.13. | Wall finish | Design the facades of buildings, considering the purpose of the buildings, the cohesive architectural appearance of the area, and long-term durability. The interior wall finishes can be minimal (for example, where construction regulations allow, walls can be unplastered and painted or impregnated), but they must meet the room's intended use. Walls in building rooms may be impregnated with clear liquids or impregnating paints. In the gym, install mirrors along one of the walls (covering the full length of the wall) with a minimum height of 2 m (raised 0.5 m from the floor). The wall covering (according to the type of covering) must match the room’s purpose, be resistant to damp cleaning, and where necessary, resistant to chemicals used for disinfecting. Where walls are to be painted, they must be painted with eco-friendly paints. Walls may also be coated with other high-quality and suitable coverings matching the purpose of the room. In sanitary units, the walls must be covered with ceramic tiles, and the cabin walls must be elevated from the floor and made of chipboard (MDP) or laminated panels (HPL), both with an aluminium frame. The participant provides descriptions of wall construction types, frame infills, and finishes etc.
1.14. | Ceiling finishing | The ceiling finishing may be minimal, but it must comply with the intended use of the room. The Participant provides information on ceiling types, structures, finishes etc.
1.15. | External doors, windows, and showcases | Where required by special regulations, protective metal grills should be installed, and access to windows from the exterior of the building should be restricted. The Participant provides information on windows, showcases, doors, gates, including sills, trims, fittings, drive mechanisms, micro-ventilation elements, and other installed components.
1.16. | Skylights | The Participant provides information on skylights, roof hatches, including trims, fittings, drive mechanisms, ventilation elements, and other installed components.
1.17. | Internal doors and windows | Internal doors, depending on the purpose, security, and number of operating cycles – metal, plastic, aluminium, or wooden (veneered). Fittings must be adapted to the designated use of the premises. Entrance doors to separate zones must be equipped with electromagnetic locks, scanning devices, and, if required, intercom systems. Doors must be designed to provide sound insulation where required, withstand increased operational loads, and be easy to operate. Access control and management from the outside will be performed for all working and other office doors, and internal exit management is expected to be with a handle/button. If required, doors may be locked with a mechanical lock. In high-traffic areas, doors must also be protected with galvanised steel plates covering up to half their height. In areas where specific architectural solutions are required for internal equipment, other protective measures may be proposed. Access to doors and movement zones must be protected from damage and accelerated material wear. Information plates must be installed on doors. Information plates must be installed on interior doors and at entrances to each floor’s rooms, allowing for easy modification of displayed information. The information to be specified on the arrows and information boards will be determined by the Public Entity. All internal doors must have locks controlled by keys. These devices are applied additionally along with access control equipment. All internal doors registered in the access control system must have locks controlled by an electronic card reader and remote controller. There must be a manual method to open the electric skis using a key in case they do not work. The Participant provides information on interior room windows, showcases, doors, gates, including sills, trims, fittings, drive mechanisms, and other installed components.
1.18. | Sun protection | External heat gain management must be planned by selecting equipment (devices) that limit direct sunlight from entering the rooms. They can be controlled mechanically when installed inside or be installed on the exterior of the window (room), in which case their control must be electric. The sun protection measures to be installed must be designed for increased operational load, as well as being easy and simple to maintain, with the ability to limit or even stop direct sunlight, while allowing diffuse light to pass through. The Participant provides information on roller blinds, awnings, and shutters, including drive mechanisms etc.
1.19. | Special built-in elements | Outdoor stair railings, handrails, joints, and covering elements must be installed from stainless steel pipes. Outdoor stair railings, handrails, joints, and covering elements must be made of stainless steel. The Participant provides information on grilles, railings, handrails, decorative and covering elements (light well covers, foot cleaning grates) et al).
1.20. | Other
1.21. | Other. Proposed by the Candidate / Participant. | The Candidate / Participant may add to the Solution / Tender its own solutions that are not in conflict with the Specification or not evaluated by the Public Entity (PE)
2. | Building internal engineering systems
2.1. | Heating systems and equipment | It is necessary to install heat consumption metering. Measuring devices must have a continuous scanning function. The possibility of adapting the heating installation for the functional separation of the military unit facility must be planned, taking into account the ability to normalise the temperature in different areas and rooms of the military unit facility by location and time, as well as the momentary increase or loss of heat, separately measuring heat consumption in separated facilities, and smoothly adjusting parameters to ensure continuous adaptation to demand, including at different times of the day. Areas where underfloor heating will be installed must be planned in such a way that they do not interfere with future furniture attachment. The participant provides a description – heat supply, heating system, heat production, heating pipelines etc. Radiators, underfloor heating, radiant heating systems etc. Metering.
2.2. | Ventilation systems and equipment | Air conditioning must be installed in work offices and server rooms. In the server rooms and uninterrupted power supply room, a separate automated precision control air conditioning system must be provided. Separate electrical panels must be provided for air conditioning equipment, and a separate grounding loop must be provided for the equipment. A constant temperature of 20–25 °C and relative humidity of 40–55% must be maintained in these rooms. The conditioning system is duplicated: one working and the other backup units. The backup air conditioner must activate automatically by rotating if the temperature in the room increases or in the event of the main air conditioner failure. In the server rooms and uninterrupted power supply room, a separate ventilation system must be provided; engineering systems not directly related to these rooms should not be installed there. Rooms must be protected from water flooding. The Participant provides information on air supply and extraction units, with or without air treatment functionality, ventilation equipment, technical air system ventilation systems, ducts and pipelines, ventilation openings and grilles, cooling systems, ducts and pipelines.
2.3. | Cooling (air conditioning) systems and equipment | The components of the cooling system must have an anti-condensation insulating layer; Water cooling system distributors (cartridges, air conditioning pipe equipment, brackets) in accessible locations must have regulating and shut-off valves to allow for system operation and control; The system must be connected to the general control system of the military unit; To cool the server rooms, precision-controlled air conditioners must be installed, which operate at low outdoor temperatures, as well as an air supply and exhaust system connected to the building’s control system. It is recommended to assess the possibility of creating the necessary engineering solutions to recover/reuse heat emitted in server rooms. The Participant provides information on selected cooling (air conditioning) system and equipment.
2.4. | Water supply and sewage systems and equipment | Anywhere sound may be heard from the wastewater piping, low-noise – thick-walled piping must be used, which must be additionally insulated; The accessibility of revisions installed on the sewage stands and the cleaning of the sewage disposal network must be planned to be free and convenient. The Participant provides information on water supply pipelines, sanitary fixtures, filters, drinking water supply, metering etc.
2.5. | Water metering installation | It is necessary to install water consumption measurement devices with a remote reading function; To ensure the required water consumption rates and the fire water supply system needs, appropriate equipment must be selected and installed Main water supply pipelines to all Military town Facilities must have separate meters and distribution. The Participant provides information on water metering etc.
2.6. | Cold water system | The water supply in the military unit's objects must be designed so that water is supplied to all collection points, taking into account the pressure, flow rate, water properties, and the purpose of the building's use, as well as peak water consumption at the same time. When different requirements are set for the parameters of the water used at the collection points, water can be supplied through independent pipelines or water supply systems, providing water with the required properties from the corresponding external water supply networks or systems, which appropriately prepare the water. Water supply and distribution must be sufficient and meet the requirements of hygiene standards and other legal acts. Water consumption metering devices with remote reading functionality must be installed. Separate metering must be installed for each system with different water consumption purposes. Sanitary equipment must be aesthetic, durable, modern, and suitable for the functional area in which it is installed, and must comply with sanitary requirements. Water must be supplied to the facilities by connecting them to the main water supply network. The equipment must be installed to ensure that the water consumption indicators for the building complex are no less than the standard values and that the fire protection water supply needs are met. If the supplied water quality is insufficient, it must be achieved through appropriate water treatment engineering solutions. The number of drinking water supply points must be determined in accordance with regulations and standards. The Participant provides information on the proposed cold water supply system.
2.7. | Hot water systems and equipment | The water supply system must ensure that water is supplied to all water usage points according to pressure, flow rate, and water characteristics requirements, peak water consumption at one time, and the designated purpose of the Military unit’s facilities. It is necessary to install water consumption measurement devices with a remote reading function; To ensure the required water consumption rates and the fire water supply system needs, appropriate equipment must be selected and installed The Participant provides information on water supply pipelines, sanitary fixtures, filters, hot water supply, metering etc.
2.8. | Domestic wastewater systems and equipment | Wastewater must be collected and directed according to economically/technically justified solutions, issued technical conditions. Toilet pots must have a water barrier inside. Water to toilet cisterns must be supplied silently (quiet operation), using no more than 6 l / 3 l of water for flushing. Urinals must have a contactless tap. In all buildings, except for the barracks washbasins near the WC (or closest to them), contactless taps with temperature limiters must be installed, as well as solutions for legionella prevention or pipe cleaning, preventing stagnant water from forming in the pipes (especially at the furthest points/water taps). In the barracks, one of the four mixers must be contactless. All sanitary devices, drain receivers, faucets, and other plumbing fixtures must be certified according to the ISO 9000 series or equivalent standard and meet the sizes specified by EN standards, with CE marking. Plumbing appliances installed in the facility must meet the following general requirements: their interior and exterior must have a smooth, easily cleanable surface (all appliances can be made of stainless steel); they must not have sharp protruding parts (in the appliance and in the fixing details); washbasins must be equipped with chrome-plated metal siphons that match the colour of the water mixing taps and faucets; toilet bowls must be equipped with seats and covers made of durable plastic. The participant provides a description – wastewater pipelines, wastewater collection facilities, wastewater treatment facilities Wastewater treatment plants
2.9. | Surface water drainage, rainwater systems, and devices | Rainwater drainage from the structures must be ensured, collected, and channelled according to the issued sewage network connection conditions. The participant provides a description – wastewater pipelines, wastewater collection facilities, wastewater treatment facilities etc.
2.10. | Plumbing appliances | Sanitary equipment must be aesthetic, durable, modern, and suitable for the functional area in which it is installed, and must comply with sanitary requirements. Sanitary infrastructure must be equipped with soap dispensers, hand dryers, paper towel dispensers, toilet paper dispensers, and automatically switched on and off lights. The Participant provides information on sanitary appliances, equipment, and systems.
2.11. | Other equipment | The Participant provides information on other equipment not included in the listed water supply and wastewater disposal systems.
2.12. | Electrical systems and equipment | Provide general artificial lighting in all sports hall spaces. In the universal sports hall, military self-defence area, and gym zones – provide dedicated lighting (general and zone-specific). Where possible, maximize the use of natural light. Locations and movement paths with few users or where users are not always present must be equipped with occupancy sensors. This is particularly important in storage and inventory areas, as well as in places with low movement. The quality of the equipment and the thoughtful placement of occupancy detectors must ensure complete convenience, as the lights must always turn on and off at the required times. Artificial lighting must be coordinated with surveillance equipment spaces and arranged so as not to dazzle the video surveillance cameras. The private partner must aim to reduce the number of lighting source models used. All equipment must be accessible for cleaning and maintenance, especially in high locations. Outdoor lighting must be controlled from the room. The lighting of auxiliary rooms must be distributed according to functional zones, but the lighting of zones related to event functions must be centralized and controlled from a dedicated room. A sufficient power capacity three-phase power supply must be planned (for all planned equipment). The electrical networks of the buildings must be designed for all types (facades, territories, fire extinguishing equipment, local television networks, fire hydrant light indicators, safety signs, call systems, light enclosures). and others) to power the lighting. Electrical cable installation must comply with the technical requirements for this system’s installation. In the building's premises, all installed control and protection devices must have a label indicating the schematic dependency and purpose. There must be a label with the name of the recipients and the line's purpose in the internal part of the door panel, on the panel by the devices. The Participant provides information on high and/or medium voltage distribution equipment. Electric power generators, including cooling, exhaust gas and fuel supply systems, central battery and uninterruptible power supply equipment, and photovoltaic systems. Cables, wires, secondary distributors, routing systems, installation devices. Fixed lights, including electric lamps. Lightning protection, lightning rod, and grounding systems. Electricity metering.
2.13. | Security alarm systems and devices | The general requirements of the system are described in Suplement 2.1 document 36 "Requirements for Electronic Protection Systems"; The Participant provides information on protection alarm system and equipment.
2.14. | Movement access control systems and devices | If card readers are installed outdoors, they must be mechanically sturdy and resistant to atmospheric conditions. In an emergency (power failure), control-operated doors must be unlockable with a key. The general requirements of the system are described in Suplement 2.1 document 36 "Requirements for Electronic Protection Systems". The Participant provides information on electromagnetic or mechanical locks. Access control system and devices.
2.16. | Video surveillance systems and equipment | The general requirements of the system are described in Suplement 2.1 document 36 "Requirements for Electronic Protection Systems". The Participant provides information on video surveillance cameras, video recording, storage, and display equipment.
2.17. | Computer and telephone networks | When designing telecommunications and computer networks and installing premises for primary equipment, the Cyber Defence Service of the Lithuanian Armed Forces (LK KGV ITT) must be provided with equipment room layouts, communication cables, networks, switching blocks, workstations, power and grounding system schemes in electronic format. When designing and constructing buildings and installing Equipment for Networks 1 and 2, representatives from the Cyber Defence Service of the Lithuanian Armed Forces (LK KGV ITT) must take part, in addition to other officials. The participant independently selects a communication provider required for PS needs and/or IP TV service provision. VS organizes the connection and service provision of the Ministry of Defence data transmission network. The Participant provides information on purpose of communication network, switch cabinet locations in the building, network switches, accessories, and other equipment.
2.18. | Automation systems and devices | A closed (local) building management system must be installed, allowing both monitoring and control of the main engineering system parameters. The accounting data analysis and processing software must be installed, designed for processing water, heat, electricity, and other meter data, generating reports, data analysis, and forecasting future needs. With the help of the installed systems, it must be possible to monitor and record the main microclimate parameters of at least five typical rooms (spaces). Meter readings must be transmitted automatically. The storage of copies of the transmitted telemetry data must be ensured. The Participant provides information on automated systems, control and monitoring devices, programming devices, sensors and actuators, communication intersection stations, and software for automated stations.
2.19. | Smoke extraction systems and equipment | The smoke extraction system and/or solution must be installed in accordance with the applicable regulations and standards. The Participant provides information on smoke extraction system, ducts, and equipment.
2.20. | Fire systems, fire detection systems, and equipment | The Participant provides information on fire detection and fire alarm systems.
2.21. | Fire extinguishing systems and equipment | The fire water supply system must comply with the applicable standards. The private partner must design an adequate number of external fire-fighting measures, considering the changes in the water supply system and fire safety standards. The private partner, considering the number of users in a specific Military Unit Object, must ensure appropriate evacuation conditions, ensuring that users can quickly and safely leave the danger zone or the area where a fire has occurred. Also, the appropriate structure, dimensions, and other technical fire safety measures must be ensured. The Participant provides information on fire suppression systems and devices.
2.22. | Gas pipeline system and equipment | The Participant provides information on gas pipeline networks, boilers, system and other equipment, metering.
2.23. | Specific use devices, other technological devices and systems | The Participant provides information on built-in elements for special purposes, signposts, informational and directional signs, colour-coded guidance systems, air compressors, liquid storage tanks etc.
2.24. | Renewable energy systems and devices are installed in the building. The system and equipment installed in the area are not evaluated here; such information is provided in the "Territory" worksheet before the field of engineering networks and systems. | The participant provides descriptions of systems and equipment, technical parameters, and details of the proposed installed equipment (location in the building, power ratings, specifications, etc.).
2.25. | Other equipment | The rooms must be equipped with a general sound system (amplifiers, speakers, microphones) to broadcast audio information from the administrative zone to the visitors in the rooms (the system must not interface with the KAS Network 1 and Network 2 networks).
3. | Other. Proposed by the Candidate / Participant. | The Candidate/Participant may supplement their Tender with the solutions that do not contradict the Specifications or are not assessed by the Public Entity (PE)
The price must match the price of part of the Facility of Supplement 2.1, document 1, worksheet 1
|  |  |  | Total (EUR, excl. VAT) | Total cost of the optimisation solutions (EUR excl. VAT). Cost of additional work or savings
REMARKS:
1. The Public Entity fills in the specifications, object data, and design task taking into account the specific features and purpose of the object part.
2. The Public Entity provides known special requirements and descriptions of objects, rooms, functional blocks, and infrastructure. If descriptions are not provided in the Public Entity tables, the Candidate/Participant must submit their tenders in accordance with applicable regulations, standards, and other legal acts.
3. The Candidate may propose and suggest possible optimisations (by suggesting to supplement the Specifications, justifying the benefits of the proposals and their impact on the price of the Tender).
4. Where possible and rational, the cost of creating a facility or other part of a building should be detailed by isolating individual parts or components of the building and specifying the anticipated cost of each respective part or component.

## 4. Development of buildings. Co
Supplement 2.1 document 10 "Technical requirements for the creation of a sports complex"
| Project name | Development of a military campus infrastructure in Klaipėda district, Kairiai
| Facility | Kairiai military town
| Type of construction | New construction
| Annex to terms & conditions | Annex 2 Specifications
| Supplement | Supplement 2.1 document 10 "Technical requirements for the creation of a sports complex"
| Supplement document (worksheet) | worksheet 4. Development of buildings. Construction
Item No. | Building part/ System/ Area | Description of special requirements for premises/areas (if applicable) | Outdoor sports complex
|  |  | Description of solutions proposed by the Candidate/Participant (reference to the annex of the Tender: Section, part, item of the Tender). | Cost of development of the solution proposed by the Candidate / Participant (EUR excl. VAT) | Possible optimisation proposed by the Candidate – additional solutions to those in the Specification (reference to the Tender document, section, paragraph, clause). Price (EUR excl. VAT) This section is to be completed only for the Initial Tender | REMARKS
| To be completed by the Public entity (PE). When submitting the Tender, the information “To be completed by the Candidate/Participant" may be suspplemented by the Candidate/Participant | to be filled by the Public Entity (if specific requirements are known and applied | to be completed by Candidate / Participant | to be completed by Candidate / Participant | To be completed by the candidate (only applicable for Initial Tender)
1. | Building structures and other elements
1.1. | Foundations | Foundations under supporting structures must be designed considering the loads, the nature of the load increase, and the foundation ground properties. The final decision on the type of foundation must be based on the results of engineering geological studies and a cost comparison of different foundation types. All fencing posts and poles must be installed with a drilled concrete foundation. In the existing underground engineering networks zone, install fence foundations manually, first evaluating and determining the location of the underground networks, including their altitude relative to the ground surface. The Participant provides information on selected foundation type, including structures, insulation, and finishing materials etc.
1.2. | Slabs on the ground. | The structure and properties of the covering must ensure the essential functional requirements throughout an economically justified service life. The participant provides information about the floor slab structure (insulation types, layers) etc.)
1.3. | Structural elements | The main criterion when choosing building materials is public safety and material durability. These materials must be used in such a way that they meet the requirements or are of better quality than those specified in the technical requirements of these Specifications. The Participant provides information on stairs, ramps, balconies, and loggia structures, including coatings etc.
1.4. | Partitions | For protection, the outdoor sports complex will be enclosed with a continuous segmental fence with lockable gates and small doors along the entire perimeter. Fence type – segmental, made of rigid 2.5 m long segments – mesh Fence height – 3 m. Segment galvanized and coated with green plastic RAL 6005. Segments are attached using special brackets to cast rectangular posts with profiles of 60 x 60 mm and wall thickness of 1.5 mm. The segmental fencing system will include two types of access gates to the area – single and double. Single gates at least 1 m wide are used for access by visitors to the enclosed area. Double gates 3 m wide are used for access by visitors and special equipment to the enclosed area. Both gate types are installed using the same segmental fence system and colour. Fencing products must come with a guarantee of no less than 10 years against rusting. Install a synthetic weather-resistant fabric or (or) mesh fence with gates for entry (exit), with a height of at least 3 m for the side fences and 4 m for the rear fences. Separation of the courts with a mobile protective measure (net), height – 3 m, ensuring safety during competitions across all courts simultaneously. The Participant provides information on Partition types, structures, finishes etc.
1.5. | Floor coverings and finishes. | Floors must be level, non-slip, crack-free, waterproof, easy to clean with a damp method, and resistant to chemical cleaners and disinfectants. Line markings for the listed sports, in accordance with the valid regulations for the respective sports. The Participant provides information on floor type, structures, finish. The main room groups are distinguished – corridors, halls, administrative rooms, service rooms, and technical auxiliary rooms etc.
1.6. | Other | Provide a rainproof metal box (standing container) with a lock to store the court, surface maintenance equipment, and sports inventory.
1.7. | Other. Proposed by the Candidate / Participant. | The Candidate / Participant may add to the Solution / Tender its own solutions that are not in conflict with the Specification or not evaluated by the Public Entity (PE)
2. | Building internal engineering systems
2.1. | Surface water drainage, rainwater systems, and devices | The following must be installed in the sports complex: A rainwater drainage system from surfaces. Covering material according to its intended purpose (the covering must dry quickly after rain (minimal absorbency), and be resistant to unstable and variable climatic conditions). The participant provides a description – wastewater pipelines, wastewater collection facilities, wastewater treatment facilities etc.
2.2. | Other equipment | The Participant provides information on other equipment not included in the listed water supply and wastewater disposal systems.
2.3. | Electrical systems and equipment | For outdoor sports complex lighting, LED luminaires must be installed, ensuring a minimum of 300 lx field surface illumination. The Participant provides information on high and/or medium voltage distribution equipment. Electric power generators, including cooling, exhaust gas and fuel supply systems, central battery and uninterruptible power supply equipment, and photovoltaic systems. Cables, wires, secondary distributors, routing systems, installation devices. Fixed lights, including electric lamps. Lightning protection, lightning rod, and grounding systems. Electricity metering.
2.4. | Video surveillance systems and equipment | The Participant provides information on video surveillance cameras, video recording, storage, and display devices.
2.5. | Fire systems, fire detection systems, and equipment | The Participant provides information on fire detection and fire alarm systems.
2.6. | Specific use devices, other technological devices and systems | The Participant provides information on built-in elements for special purposes, signposts, informational and directional signs, colour-coded guidance systems, air compressors, liquid storage tanks etc.
2.7. | Other equipment
3. | Other. Proposed by the Candidate / Participant. | The Candidate/Participant may supplement their Tender with the solutions that do not contradict the Specifications or are not assessed by the Public Entity (PE)
The price must match the price of part of the Facility of Supplement 2.1, document 1, worksheet 1
|  |  |  | Total (EUR, excl. VAT) | Total cost of the optimisation solutions (EUR excl. VAT). Cost of additional work or savings
REMARKS:
1. The Public Entity fills in the specifications, object data, and design task taking into account the specific features and purpose of the object part.
2. The Public Entity provides known special requirements and descriptions of objects, rooms, functional blocks, and infrastructure. If descriptions are not provided in the Public Entity tables, the Candidate/Participant must submit their tenders in accordance with applicable regulations, standards, and other legal acts.
3. The Candidate may propose and suggest possible optimisations (by suggesting to supplement the Specifications, justifying the benefits of the proposals and their impact on the price of the Tender).
4. Where possible and rational, the cost of creating a facility or other part of a building should be detailed by isolating individual parts or components of the building and specifying the anticipated cost of each respective part or component.

## 5. Development of buildings. Co
Supplement 2.1 document 10 "Technical requirements for the creation of a sports complex"
| Project name | Development of a military campus infrastructure in Klaipėda district, Kairiai
| Facility | Kairiai military town
| Type of construction | New construction
| Annex to terms & conditions | Annex 2 Specifications
| Supplement | Supplement 2.1 document 10 "Technical requirements for the creation of a sports complex"
| Supplement document (worksheet) | worksheet 5. Development of buildings. Construction
Item No. | Building part/ System/ Area | Description of special requirements for premises/areas (if applicable) | Stadium
|  |  | Description of solutions proposed by the Candidate/Participant (reference to the annex of the Tender: Section, part, item of the Tender). | Cost of development of the solution proposed by the Candidate / Participant (EUR excl. VAT) | Possible optimisation proposed by the Candidate – additional solutions to those in the Specification (reference to the Tender document, section, paragraph, clause). Price (EUR excl. VAT) This section is to be completed only for the Initial Tender | REMARKS
| To be completed by the Public entity (PE). When submitting the Tender, the information “To be completed by the Candidate/Participant" may be suspplemented by the Candidate/Participant | to be filled by the Public Entity (if specific requirements are known and applied | to be completed by Candidate / Participant | to be completed by Candidate / Participant | To be completed by the candidate (only applicable for Initial Tender)
1. | Building structures and other elements
1.1. | Foundations | Foundations under supporting structures must be designed considering the loads, the nature of the load increase, and the foundation ground properties. The final decision on the type of foundation must be based on the results of engineering geological studies and a cost comparison of different foundation types. All fencing posts and poles must be installed with a drilled concrete foundation. The Participant provides information on selected foundation type, including structures, insulation, and finishing materials etc.
1.2. | Slabs on the ground. | Provide the necessary foundations for the football pitch's artificial surface and the running tracks. The structure and properties of the covering must ensure the essential functional requirements throughout an economically justified service life. The participant provides information about the floor slab structure (insulation types, layers) etc.)
1.3. | Structural elements | The main criterion when choosing building materials is public safety and material durability. These materials must be used in such a way that they meet the requirements or are of better quality than those specified in the technical requirements of these Specifications. The Participant provides information on stairs, ramps, balconies, and loggia structures, including coatings etc.
1.4. | Partitions | Provide internal fencing for the stadium and its auxiliary areas. The fence height should be such that it ensures the ball does not go beyond the stadium's boundary. The Participant provides information on Partition types, structures, finishes etc.
1.5. | Floor coverings and finishes. | Line markings for the listed sports, in accordance with the valid regulations for the respective sports. Provide the installation of an artificial surface football pitch (FIFA licensed). The Participant provides information on floor type, structures, finish. The main room groups are distinguished – corridors, halls, administrative rooms, service rooms, and technical auxiliary rooms etc.
1.6. | Other | Provide a room (garage) of 28 m² for stadium equipment, sports inventory, and surface maintenance equipment, with self-propelled access to it from the stadium side.
1.7. | Other. Proposed by the Candidate / Participant. | The Candidate / Participant may add to the Solution / Tender its own solutions that are not in conflict with the Specification or not evaluated by the Public Entity (PE)
2. | Building internal engineering systems
2.1. | Surface water drainage, rainwater systems, and devices | A rainwater drainage system from surfaces must be installed. Provide an appropriate running track surface for use in all seasons. Covering material according to its intended purpose (the covering must dry quickly after rain (minimal absorbency), and be resistant to unstable and variable climatic conditions). The participant provides a description – wastewater pipelines, wastewater collection facilities, wastewater treatment facilities etc.
2.2. | Other equipment | The Participant provides information on other equipment not included in the listed water supply and wastewater disposal systems.
2.3. | Electrical systems and equipment | For outdoor sports complex lighting, LED luminaires must be installed, ensuring a minimum of 300 lx field surface illumination. The Participant provides information on high and/or medium voltage distribution equipment. Electric power generators, including cooling, exhaust gas and fuel supply systems, central battery and uninterruptible power supply equipment, and photovoltaic systems. Cables, wires, secondary distributors, routing systems, installation devices. Fixed lights, including electric lamps. Lightning protection, lightning rod, and grounding systems. Electricity metering.
2.4. | Video surveillance systems and equipment | The Participant provides information on video surveillance cameras, video recording, storage, and display devices.
2.5. | Specific use devices, other technological devices and systems | The Participant provides information on built-in elements for special purposes, signposts, informational and directional signs, colour-coded guidance systems, air compressors, liquid storage tanks etc.
2.6. | Other equipment
3. | Other. Proposed by the Candidate / Participant. | The Candidate/Participant may supplement their Tender with the solutions that do not contradict the Specifications or are not assessed by the Public Entity (PE)
The price must match the price of part of the Facility of Supplement 2.1, document 1, worksheet 1
|  |  |  | Total (EUR, excl. VAT) | Total cost of the optimisation solutions (EUR excl. VAT). Cost of additional work or savings
REMARKS:
1. The Public Entity fills in the specifications, object data, and design task taking into account the specific features and purpose of the object part.
2. The Public Entity provides known special requirements and descriptions of objects, rooms, functional blocks, and infrastructure. If descriptions are not provided in the Public Entity tables, the Candidate/Participant must submit their tenders in accordance with applicable regulations, standards, and other legal acts.
3. The Candidate may propose and suggest possible optimisations (by suggesting to supplement the Specifications, justifying the benefits of the proposals and their impact on the price of the Tender).
4. Where possible and rational, the cost of creating a facility or other part of a building should be detailed by isolating individual parts or components of the building and specifying the anticipated cost of each respective part or component.