## 1. Development of buildings. Ne
Supplement 2.1 document 12 "Technical requirements for the creation of repair workshop"
| Project name |  | Development of a military campus infrastructure in Klaipėda district, Kairiai
| Facility |  | Kairiai military town
| Type of construction |  | New construction
| Annex to terms & conditions |  | Annex 2 Specifications
| Supplement |  | Supplement 2.1 document 12 "Technical requirements for the creation of repair workshop"
| Supplement document (worksheet) |  | worksheet 1. Development of buildings. Needs
Item No. | The name of the room/space/functional block | Number of places | Phones connected to the KATT | Computer networks are connected to the unit's network 2 | Computer networks are connected to the KAS network 1 | Number of computerised workstations | Approximate area (sq. m) (if needed to determine) | The significance level of the room/space/functional block (A, B, C and D) | Description of special requirements for premises/areas (if applicable) | The area of the premises/space/functional block in square metres proposed by the Candidate/Participant | numbering of premises according to the explanations on the drawings proposed by the Candidate/Participant | Cost of development of the solution proposed by the Candidate / Participant (EUR excl. VAT) | Furniture/equipment inventory |  |  |  | Possible optimisation proposed by the Candidate – additional solutions to those in the Specification (reference to the Tender document, section, paragraph, clause). Price (EUR excl. VAT) This section is to be completed only for the Initial Tender | REMARKS
[13 empty] | Description of the building's furniture/equipment inventory needs and Special Requirements (if any) | The planned furniture/equipment inventory is purchased by *PS, **PS, or VS | The price of furniture and equipment proposed by the Candidate/Participant for the investor (which is purchased by the Private Entity) (*PS, **PS)) (EUR excl. VAT) | Cost for the installation of the furniture and equipment inventory proposed by the Candidate/Participant (*PS, **PS) (EUR excl. VAT)
| To be completed by the Public entity (PE). When submitting the Tender, the information “To be completed by the Candidate/Participant" may be suspplemented by the Candidate/Participant | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | to be completed by Candidate / Participant | to be completed by Candidate / Participant | to be completed by Candidate / Participant | To be completed by Public entity | To be completed by Public entity | to be completed by Candidate / Participant | to be completed by Candidate / Participant | To be completed by the candidate (only applicable for Initial Tender)
1. | Repair workshop (type 1)
1.1. | Administrative area |  | 15 | 0 | 15 | 37
1.1.1. | Office | 2 | 2 | - | 2 | 2 | 16 | C | the walls and ceilings must be built of brick, blocks, or constructed from metal sheets, solid wood, or similar materials providing equivalent resistance to break-ins. the door leaf and frame must be made of metal sheets less than 2 mm thick, solid wood, particleboard, plywood, glass, or similar materials ensuring equivalent resistance to burglary; the door must be fitted with a single lock with a cylindrical core or a lever lock. window frames must be made of durable material, and the glass must be coated with a protective film. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of access to the building and building entrance, Access control system – not provided. |  |  |  | Provide spaces for office furniture sets No. 2 and No. 3 (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.1.2. | Office | 3 | 3 | - | 3 | 3 | 18 | C |  |  |  |  | Provide spaces for office furniture sets No. 2 – (1 pcs) and No. 3 – (1 pcs) (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.1.3. | Office | 3 | 3 | - | 3 | 3 | 18 | C |  |  |  |  | Provide spaces for office furniture sets No. 2 – (1 pcs) and No. 3 – (1 pcs) (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.1.4. | Office | 3 | 3 | - | 3 | 3 | 18 | C |  |  |  |  | Provide spaces for office furniture sets No. 2 – (1 pcs) and No. 3 – (1 pcs) (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.1.5. | Office | 3 | 3 | - | 3 | 3 | 18 | C |  |  |  |  | Provide spaces for office furniture sets No. 2 – (1 pcs) and No. 3 – (1 pcs) (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.1.6. | Meeting room | 10 | 1 | - | 1 | 1 | 15 | C | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide a meeting room set No. 6 (according to document 28 of Annex 2 Supplement 2 of the Terms) | *PS
1.1.7. | Recreation room | - | - | - | - | 20 | 4 | D | *Magnetic contacts for security alarm systems are planned for the movable parts of the building’s exterior windows and doors and are assigned to the corridor area. |  |  |  | Recreation furniture set (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.1.8. | Changing room | 45 | - | - | - | 2 | 3 | C |  |  |  |  | Changing lockers must be provided – 45 units.Provide all necessary equipment for the room to function. | *PS
1.1.9. | Shower room | - | - | - | - | - | 10 | C | Provide spaces and necessary connections for the industrial washing machine with dryer set. |  |  |  | Provide all necessary equipment for the room to function. | PS
1.1.10. | Office | 2 | 2 | - | 2 | 2 | 16 | C | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide spaces for office furniture sets No. 2, and No. 3 (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.1.11. | Office | 2 | 2 | - | 2 | 2 | 16 | C |  |  |  |  | Provide spaces for office furniture sets No. 2 – (1 pcs) and No. 3 – (1 pcs) (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.2. | Administrative area |  | 15 | 0 | 15 | 37 | 120
1.2.1. | Office | 2 | 2 | - | 2 | 2 | 16 | C | the walls and ceilings must be built of brick, blocks, or constructed from metal sheets, solid wood, or similar materials providing equivalent resistance to break-ins. the door leaf and frame must be made of metal sheets less than 2 mm thick, solid wood, particleboard, plywood, glass, or similar materials ensuring equivalent resistance to burglary; the door must be fitted with a single lock with a cylindrical core or a lever lock. window frames must be made of durable material, and the glass must be coated with a protective film. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of access to the building and building entrance, Access control system – not provided. |  |  |  | Provide spaces for office furniture sets No. 2 and No. 3 (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.2.2. | Office | 3 | 3 | - | 3 | 3 | 18 | C |  |  |  |  | Provide spaces for office furniture sets No. 2 – (1 pcs) and No. 3 – (1 pcs) (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.2.3. | Office | 3 | 3 | - | 3 | 3 | 18 | C |  |  |  |  | Provide spaces for office furniture sets No. 2 – (1 pcs) and No. 3 – (1 pcs) (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.2.4. | Office | 3 | 3 | - | 3 | 3 | 18 | C |  |  |  |  | Provide spaces for office furniture sets No. 2 – (1 pcs) and No. 3 – (1 pcs) (according to document 29 of Supplement 2 of Annex 2 of the Terms) | *PS
1.2.5. | Office | 3 | 3 | - | 3 | 3 | 18 | C |  |  |  |  | Provide spaces for office furniture sets No. 2 – (1 pcs) and No. 3 – (1 pcs) (according to document 29 of Supplement 2 of Annex 2 of the Terms) | *PS
1.2.6. | Meeting room | 10 | 1 | - | 1 | 1 | 15 | C | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide a meeting room set No. 6 (according to document 28 of Annex 2 Supplement 2 of the Terms) | *PS
1.2.7. | Recreation room | - | - | - | - | 20 | 4 | D | *Magnetic contacts for security alarm systems are planned for the movable parts of the building’s exterior windows and doors and are assigned to the corridor area. |  |  |  | Recreation furniture set (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.2.8. | Changing room | 45 | - | - | - | 2 | 3 | C |  |  |  |  | Individual lockers must be installed – 45 units. Provide all necessary equipment for the room to function. | *PS
1.2.9. | Shower room | - | - | - | - | - | 10 | C | Provide spaces and necessary connections for the industrial washing machine with dryer set. |  |  |  |  | *PS
1.3. | Special-purpose zone |  | 0 | 0 | 0 | 0 | 782 |  | *Security systems for the premises are installed in accordance with document 36 of Annex 2.1, "Requirements for the installation of electronic security systems" Type 1 room. Video surveillance – general monitoring of building access points and entrances, (except for the technical repair room), Access control system – not planned.
1.3.1. | Machinery repair room | 4 | - | - | - | - | 570 | C | Technical repair workshops should be planned next to each other, in a mirrored arrangement, with a common crane. Partitioned with a 4 m high mesh barrier. A 15 t overhead crane must be provided in the room, serving 8 repair stations (one crane for two workshops). The interior of the room is monitored with no fewer than 6 video cameras (the exact number will be coordinated during the design tender phase) |  |  |  | Provide the necessary furniture and equipment for the room's functionality. (according to document 32 of Supplement 2 of Annex 2.1 of the Terms) | PS
1.3.2. | Storage room | - | - | - | - | - | 20 | C |  |  |  |  | Provide racks (according to document 26 of Annex 2 Supplement 2.1 of the Terms). | *PS
1.3.3. | Storage room | - | - | - | - | - | 50 | C |  |  |  |  | Provide racks (according to document 26 of Annex 2 Supplement 2.1 of the Terms). | *PS
1.3.4. | Storage room | - | - | - | - | - | 20 | C |  |  |  |  | Provide racks (according to document 26 of Annex 2 Supplement 2.1 of the Terms). | *PS
1.3.5. | Storage room | - | - | - | - | - | 12 | C |  |  |  |  | Provide racks (according to document 26 of Annex 2 Supplement 2.1 of the Terms). | *PS
1.3.5. | Storage room | - | - | - | - | - | 20 | C |  |  |  |  | Provide racks (according to document 26 of Annex 2 Supplement 2.1 of the Terms). | *PS
1.3.6. | Battery maintenance room | - | - | - | - | - | 20 | C | *Motion sensors and magnetic contacts are selected based on the explosion/flammability classification of the premises |  |  |  | Provide the necessary furniture and equipment for the room's functionality. (according to document 32 of Supplement 2 of Annex 2.1 of the Terms) | **PS
1.3.7. | Tire installation room | - | - | - | - | - | 25 | C |  |  |  |  | Provide the necessary furniture and equipment for the room's functionality. (according to document 32 of Supplement 2 of Annex 2.1 of the Terms) | **PS
1.3.8. | Metalworking room | - | - | - | - | - | 25 | C |  |  |  |  | Provide the necessary furniture and equipment for the room's functionality. (according to document 32 of Supplement 2 of Annex 2.1 of the Terms) | **PS
1.3.9. | Special-purpose room | - | - | - | - | - | 20 | C |  |  |  |  | Provide the necessary furniture and equipment for the room's functionality. (according to document 32 of Supplement 2 of Annex 2.1 of the Terms) | **PS
1.4. | Special-purpose zone |  | 0 | 0 | 0 | 0 | 787 |  | *Security systems for the premises are installed in accordance with document 36 of Annex 2.1, "Requirements for the installation of electronic security systems" Type 1 room. Video surveillance – general monitoring of building access points and entrances, (except for the technical repair room), Access control system – not planned.
1.4.1. | Machinery repair room | 4 | - | - | - | - | 570 | C | Technical repair workshops should be planned next to each other, in a mirrored arrangement, with a common crane. Partitioned with a 4 m high mesh barrier. A 15 t overhead crane must be provided in the room, serving 8 repair stations (one crane for two workshops). The interior of the room is monitored with no fewer than 6 video cameras (the exact number will be coordinated during the design tender phase) |  |  |  | Provide the necessary furniture and equipment for the room's functionality. (according to document 32 of Supplement 2 of Annex 2.1 of the Terms) | PS
1.4.2. | Storage room | - | - | - | - | - | 20 | C |  |  |  |  | Provide racks (according to document 26 of Annex 2 Supplement 2.1 of the Terms). | *PS
1.4.3. | Storage room | - | - | - | - | - | 50 | C |  |  |  |  | Provide racks (according to document 26 of Annex 2 Supplement 2.1 of the Terms). | *PS
1.4.4. | Storage room | - | - | - | - | - | 20 | C |  |  |  |  | Provide racks (according to document 26 of Annex 2 Supplement 2.1 of the Terms). | *PS
1.4.5. | Storage room | - | - | - | - | - | 12 | C |  |  |  |  | Provide racks (according to document 26 of Annex 2 Supplement 2.1 of the Terms). | *PS
1.4.6. | Storage room | - | - | - | - | - | 20 | C |  |  |  |  | Provide racks (according to document 26 of Annex 2 Supplement 2.1 of the Terms). | *PS
1.4.7. | Battery maintenance room | - | - | - | - | - | 20 | C | *Motion sensors and magnetic contacts are selected based on the explosion/flammability classification of the premises |  |  |  | Provide the necessary furniture and equipment for the room's functionality. (according to document 32 of Supplement 2 of Annex 2.1 of the Terms) | PS
1.4.8. | Tire installation room | - | - | - | - | - | 25 | C |  |  |  |  | Provide the necessary furniture and equipment for the room's functionality. (according to document 32 of Supplement 2 of Annex 2.1 of the Terms) | PS
1.4.9. | Metalworking room | - | - | - | - | - | 25 | C |  |  |  |  | Provide the necessary furniture and equipment for the room's functionality. (according to document 32 of Supplement 2 of Annex 2.1 of the Terms) | PS
1.4.10. | Special-purpose room | - | - | - | - | - | 25 | C |  |  |  |  | Provide the necessary furniture and equipment for the room's functionality. (according to document 32 of Supplement 2 of Annex 2.1 of the Terms) | PS
1.5. | Building engineering system rooms |  | 0 | 0 | 0 | 0 | 60
1.5.1. | Technical rooms | - | - | - | - | - | 40 | C | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 1 room. Video surveillance – general monitoring of building access points and entrances, Access control system – not planned.
1.5.2. | Electronic security systems switch room | - | - | - | - | - | 6 | A | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 4 room.
1.5.3. | Switching room (communication distribution point) | - | - | - | - | - | 14 | A
1.5.4. | Compressor | - | - | - | - | - | 4 | C
1.6. | Other rooms |  | 0 | 0 | 0 | 0 | 275
1.6.1. | Corridor | - | - | - | - | - | 275 | C | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 1 room Video surveillance – general monitoring of building access points and entrances, Access control system (including building access) – not planned.
1.7. | Other. Proposed by the Candidate / Participant. | [7 empty] | The Candidate/Participant may supplement their Tender with the solutions that do not contradict the Specifications or are not assessed by the Public Entity (PE)
| Total building area |  | 30 | 0 | 30 | 74 | 2176
The price must match the price of part of the Facility of Supplement 2.1, document 1, worksheet 1
[12 empty] | Total (EUR, excl. VAT) |  |  |  |  | Total cost of the optimisation solutions (EUR excl. VAT). Cost of additional work or savings
REMARKS:
1. The Public Entity fills in the specifications, object data, and design task taking into account the features and purpose of the object.
2. The Public Entity provides known special requirements and descriptions of objects, rooms, spaces, functional blocks, and infrastructure. If descriptions are not provided in the Public Entity tables, the Candidate/Participant must submit their tenders in accordance with applicable regulations, standards, and other legal acts.
3. The Candidate/Participant may propose and suggest possible optimisations in their solutions (by suggesting to supplement the Specifications, justifying the benefits of the proposals and their impact on the price of the Tender).
4. The Public Entity classifies rooms/ spaces/ functional blocks by significance levels into functional sector significance levels A, B, C, and D (Specifications section "Functional sectors").
5. The areas provided in the table are approximate and may change depending on the implementation of regulatory acts and the requirements of the Specifications.
6. The technological rooms must be equipped with an air conditioning system, ensuring the proper operating conditions for the equipment installed in these rooms. Parameters are selected according to the recommendations of computer network equipment manufacturers. Temperature deviations in the rooms must be automatically recorded in the Registration Tool.
7. The size of technological premises indicated in the table is approximate, it is adjusted by evaluating the planned equipment quantities to be installed. The size of the room must allow easy access to the switchgear cabinets and equipment maintenance.
10. Technological rooms should not be located beneath sanitary facilities or in other areas where there is a high risk of flooding.
11. If necessary to clarify the solutions, the Participant may add rows to their table.
12. * The PS must provide for a one-time furniture purchase and warranty maintenance for a period of 5 years
13 The PS must provide equipment/furniture that is mandatory (or necessary) for the proper functioning (use) of buildings/premises, in accordance with legal acts/regulations, the Private Entity’s solutions, etc., including their further technical maintenance throughout the entire Contract period

## 1. Creation of buildings. Needs
Supplement 2.1 document 12 "Technical requirements for the creation of repair workshop"
| Project name |  | Development of a military campus infrastructure in Klaipėda district, Kairiai
| Facility |  | Kairiai military town
| Type of construction |  | New construction
| Annex to terms & conditions |  | Annex 2 Specifications
| Supplement |  | Supplement 2.1 document 12 "Technical requirements for the creation of repair workshop"
| Supplement document (worksheet) |  | worksheet 2. Development of buildings. Needs
| The name of the room/space/functional block | Total number of places | Phones connected to the KATT | Computer networks are connected to the unit's network 2 | Computer networks are connected to the KAS network 1 | Number of computerised workstations | Approximate area (sq. m) (if needed to determine) | The significance level of the room/space/functional block (A, B, C and D) | Description of special requirements for premises/areas (if applicable) | The area of the premises/space/functional block in square metres proposed by the Candidate/Participant | numbering of premises according to the explanations on the drawings proposed by the Candidate/Participant | Cost of development of the solution proposed by the Candidate / Participant (EUR excl. VAT) | Furniture/equipment inventory |  |  |  | Possible optimisation proposed by the Candidate – additional solutions to those in the Specification (reference to the Tender document, section, paragraph, clause). Price (EUR excl. VAT) This section is to be completed only for the Initial Tender | REMARKS
Item No. | [12 empty] | Description of the building's furniture/equipment inventory needs and Special Requirements (if any) | The planned furniture/equipment inventory is purchased by *PS, **PS, or VS | The price of furniture and equipment proposed by the Candidate/Participant for the investor (which is purchased by the Private Entity) (*PS, **PS)) (EUR excl. VAT) | Cost for the installation of the furniture and equipment inventory proposed by the Candidate/Participant (*PS, **PS) (EUR excl. VAT)
| To be completed by the Public entity (PE). When submitting the Tender, the information “To be completed by the Candidate/Participant" may be suspplemented by the Candidate/Participant | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | to be completed by Candidate / Participant | to be completed by Candidate / Participant | to be completed by Candidate / Participant | To be completed by Public entity | To be completed by Public entity | to be completed by Candidate / Participant | to be completed by Candidate / Participant | To be completed by the candidate (only applicable for Initial Tender)
1. | Repair workshop (type 2)
1.1. | Administrative area |  | 22 | 0 | 22 | 23 | 614
1.1.1. | Office | 3 | 3 | - | 3 | 3 | 20 | C | The walls and ceilings must be built of brick, blocks, or constructed from metal sheets, solid wood, or similar materials providing equivalent resistance to break-ins. The door leaf and frame must be made of metal sheets less than 2 mm thick, solid wood, particleboard, plywood, glass, or similar materials ensuring equivalent resistance to burglary. Doors must be equipped with one lock with a cylindrical core or a lever lock. Window frames must be made of durable material, and the glass must be coated with a protective film. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide spaces for office furniture sets No. 2 and No. 3 (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.1.2. | Office | 3 | 3 | - | 3 | 3 | 20 | C |  |  |  |  | Provide spaces for office furniture sets No. 2 – (1 pcs) and No. 3 – (1 pcs) (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.1.3. | Office | 3 | 3 | - | 3 | 3 | 20 | C |  |  |  |  | Provide spaces for office furniture sets No. 2 – (1 pcs) and No. 3 – (1 pcs) (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.1.4. | Office | 3 | 3 | - | 3 | 3 | 20 | C |  |  |  |  | Provide spaces for office furniture sets No. 2 – (1 pcs) and No. 3 – (1 pcs) (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.1.5. | Office | 3 | 3 | - | 3 | 3 | 20 | C |  |  |  |  | Provide spaces for office furniture sets No. 2 – (1 pcs) and No. 3 – (1 pcs) (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.1.6. | Technical library and archive | 1 | 1 | - | 1 | 1 | 35 | C | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide spaces for office furniture sets No. 2 – (1 pcs) and No. 3 – (2 pcs) (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.1.7. | Workshop supervisor’s office | 1 | 1 | - | 1 | 2 | 15 | C | The workstation must have a total of 6 units 230 V sockets and 2 units of computer networks. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide spaces for office furniture sets No. 2 – (1 pcs) and No. 3 – (1 pcs) (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.1.8. | Workshop supervisor’s office | 1 | 1 | - | 1 | 2 | 15 | C | The workstation must have a total of 6 units 230V sockets and 2 units of computer networks. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide spaces for office furniture sets No. 2 – (1 pcs) and No. 3 – (1 pcs) (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.1.9. | Administrative room for diagnostics and technical inspection line staff | 3 | 3 | - | 3 | 2 | 20 | C | The workstation must have a total of 6 units 230 V sockets and 2 units of computer networks. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide spaces for office furniture sets No. 2 – (1 pcs) and No. 3 – (1 pcs) (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.1.10. | Meeting room | 1 | 1 | - | 1 | 1 | 120 | C | A designated space must be provided for a ceiling-mounted video projector for displaying visual information. Two magnetic whiteboards must be installed on the wall. The necessary electrical connections for the equipment must be provided. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide a meeting room set No. 6 (according to document 28 of Annex 2 Supplement 2 of the Terms) | *PS
1.1.10. | Recreation room | - | - | - | - | - | 20 | D | A domestic space must be equipped (sink with hot and cold water connections and dispensers for disposable towels and washing agents, 2 kitchen cabinets, space for a refrigerator). A TV connection point (3 electrical socket outlets and an RJ45 socket for the television network) must be provided. *Magnetic contacts for security alarm systems are planned for the movable parts of the building’s exterior windows and doors and are assigned to the corridor area. |  |  |  | Recreation furniture set (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.1.11. | Recreation room (for workers) | - | - | - | - | - | 85 | D | A domestic space must be equipped (sink with hot and cold water connections and dispensers for disposable towels and washing agents, 2 kitchen cabinets, space for a refrigerator). A TV connection point (3 electrical socket outlets and an RJ45 socket for the television network) must be provided. *Magnetic contacts for security alarm systems are planned for the movable parts of the building’s exterior windows and doors and are assigned to the corridor area. |  |  |  | Recreation furniture set (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.1.11. | Changing room (men’s) | - | - | - | - | - | 150 | C | The changing room must be divided into two sections for changing into specialised clothing for painting and welding work. *Magnetic contacts for security alarm systems are planned for the movable parts of the building’s exterior windows and doors and are assigned to the corridor area. |  |  |  | Provide all required equipment and furniture required for the room's functionality. | PS
1.1.11. | Changing room (women’s) | - | - | - | - | - | 20 | C | *Magnetic contacts for security alarm systems are planned for the movable parts of the building’s exterior windows and doors and are assigned to the corridor area. |  |  |  | Provide all required equipment and furniture required for the room's functionality. | PS
1.1.11. | Showers | - | - | - | - | - | 14 | C | *Magnetic contacts for security alarm systems are planned for the movable parts of the building’s exterior windows and doors and are assigned to the corridor area. |  |  |  | Provide all required equipment and furniture required for the room's functionality. | PS
1.1.12. | WC (men's) | - | - | - | - | - | 10 | C |  |  |  |  | Provide all required equipment and furniture required for the room's functionality. | PS
1.1.13. | WC (women's) | - | - | - | - | - | 10 | C |  |  |  |  | Provide all required equipment and furniture required for the room's functionality. | PS
1.2. | Special-purpose zone | [7 empty] | Provide technological solutions and descriptions for the rooms.
1.2.1. | Workshop for repairing electrical systems of vehicles | - | - | - | - | - | 42 | C | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 1 room. Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide racks (according to document 26 of Annex 2 Supplement 2.1 of the Terms). | *PS
1.2.2. | Workshop for repairing armoured vehicle communication systems | - | - | - | - | - | 42 | C | The premises must comply with the requirements for Security Zone II. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 4 room. |  |  |  | Provide the necessary furniture and equipment for the room's functionality. (according to document 33 of Supplement 2 of Annex 2.1 of the Terms) | PS
1.2.3. | Armoured vehicle optics repair room | - | - | - | - | - | 42 | C | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide the necessary furniture and equipment for the room's functionality. (according to document 33 of Supplement 2 of Annex 2.1 of the Terms) | PS
1.2.4. | Storage room (spare parts) | - | - | - | - | - | 36 | C | 1. Efficient use of the designated space must include areas for metal shelving units to store stored items. The height must allow for the vertical stacking of three Euro pallets with cargo and accommodate a forklift, but must not be less than 3.8 metres. 2. The premises must be designed to ensure easy access from the vehicle repair area: technical solutions must provide the possibility to transfer stored items to the vehicle repair premises easily and over the shortest distance, and allow direct access to the storage rooms from outside, i.e., not through the vehicle repair premises. 3. A stable microclimate must be maintained in the premises: 45% humidity and an air temperature of +15°C must be ensured. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 1 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide racks (according to document 26 of Annex 2 Supplement 2.1 of the Terms). | *PS
1.2.5. | Tool room | - | - | - | - | - | 20 | C |  |  |  |  | Provide racks (according to document 26 of Annex 2 Supplement 2.1 of the Terms). | *PS
1.2.6. | Oil and special fluids storage | - | - | - | - | - | 50 | C |  |  |  |  | Provide the necessary furniture and equipment for the room's functionality. (according to document 33 of Supplement 2 of Annex 2.1 of the Terms) | PS
1.2.7. | Tyre repair and servicing room | - | - | - | - | - | 110 | C |  |  |  |  | Provide the necessary furniture and equipment for the room's functionality. (according to document 33 of Supplement 2 of Annex 2.1 of the Terms) | PS
1.2.8. | Tarpaulin repair room | - | - | - | - | - | 70 | C | Additional ventilation must be provided near sewing machines. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 1 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide the necessary furniture and equipment for the room's functionality. (according to document 33 of Supplement 2 of Annex 2.1 of the Terms) | PS
1.2.9. | Welding and metal cutting room | - | - | - | - | - | 200 | C | Efficient use of the designated space must include areas for metal shelving units to store stored items. The height must allow for the vertical stacking of three Euro pallets with cargo and accommodate a forklift, but must not be less than 3.8 metres. |  |  |  | Provide the necessary furniture and equipment for the room's functionality. (according to document 33 of Supplement 2 of Annex 2.1 of the Terms) | PS
1.2.10. | Turner-miller workshop | - | - | - | - | - | 60 | C | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 1 room. Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide the necessary furniture and equipment for the room's functionality. (according to document 33 of Supplement 2 of Annex 2.1 of the Terms) | PS
1.2.11. | Battery room | - | - | - | - | - | 8 | C | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 1 room, motion sensors and magnetic contacts are selected based on the explosion/flammability classification of the premises, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide the necessary furniture and equipment for the room's functionality. (according to document 33 of Supplement 2 of Annex 2.1 of the Terms) | PS
1.2.12. | Electrolyte room | - | - | - | - | - | 8 | C | Ventilation with air extraction (hood), filtration system (for acid batteries), liquid welding trough (ceramic). Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 1 room, motion sensors and magnetic contacts are selected based on the explosion/flammability classification of the premises, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide the necessary furniture and equipment for the room's functionality. (according to document 33 of Supplement 2 of Annex 2.1 of the Terms) | PS
1.2.13. | Compressor | - | - | - | - | - | 20 | C | Primary and backup screw compressors with a dryer (air intake from outside), ventilation system. HVAC and security systems must be installed in accordance with document 36 of Annex 2.1, "Requirements for the Installation of Electronic Security Systems," classified as a Type 1 facility. Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide the necessary furniture and equipment for the room's functionality. (according to document 33 of Supplement 2 of Annex 2.1 of the Terms) | PS
1.2.14. | Repair workshop | - | - | - | - | - | 2500 | C | 1. Four entrances/exits must be provided for heavy vehicles. 2. The premises must include four repair workstations, each with a minimum area of 142.5 m². Required exterior gate dimensions: height – no less than 4.8 m; width – no less than 4.8 m. Pedestrian doors must be integrated into the gates. 3. The premises must be equipped with an overhead crane (or cranes) with a lifting capacity of 15 tonnes and a lifting height of 7.5 metres from floor level 4. Scissor lifts must be installed in the premises (2 pcs), A total of two identical scissor lifts for heavy vehicles must be installed, each with a lifting capacity of at least 45 tonnes 5. A mobile four-column lift with a lifting capacity of at least 22 tonnes must be provided in the premises. 6. The zone must include washbasins (2 pcs) with cold and hot water connections, a mirror next to the washbasin, and dispensers for disposable towels and washing supplies 7. A centralised oil/fluid supply system must be installed in the premises, covering each workstation 8. Two service pits must be provided in the premises: 10,0x1,0x1,60 m. with stairs. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 1 room. Video surveillance – the interior of the premises must be monitored with no fewer than 6 to 8 cameras (exact number to be determined during the design proposal phase). Access control system – not required. |  |  |  | Provide the necessary furniture and equipment for the room's functionality. (according to document 33 of Supplement 2 of Annex 2.1 of the Terms) | PS
1.2.15. | Painting preparation room | - | - | - | - | - | 70 | C | HVAC, lighting, guidance, special flooring, lift gates, direct access to the painting chamber. |  |  |  | Provide the necessary furniture and equipment for the room's functionality. (according to document 33 of Supplement 2 of Annex 2.1 of the Terms) | **PS
1.2.16. | Diagnostics and technical inspection room | - | - | - | - | - | 150 | C | Technical inspection line (suspension test stand). Bottom lift, ventilation, lighting, exhaust gas extraction, overhead crane with 16 t and 10 t capacities, scissor lift with 40 t capacity. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 1 room. Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide the necessary furniture and equipment for the room's functionality. (according to document 33 of Supplement 2 of Annex 2.1 of the Terms) | PS
1.2.18. | Wash room | - | - | - | - | - | 150 | C | Internal wall waterproofing, water supply – sewage system, washing equipment, ventilation, lighting. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 1 room. Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide the necessary furniture and equipment for the room's functionality. (according to document 33 of Supplement 2 of Annex 2.1 of the Terms) | PS
1.2.19. | Painting room (water-based paints) | - | - | - | - | - | 100 | C | Painting/drying booth with a separate filtration system (for trucks), air supply, ventilation, lighting, specialised flooring. |  |  |  | Provide the necessary furniture and equipment for the room's functionality. (according to document 33 of Supplement 2 of Annex 2.1 of the Terms) | PS
1.2.20. | Paint preparation room | - | - | - | - | - | 10 | C | Apint mixing equipment, scales, lighting, guidance, special flooring. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 1 room. Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide the necessary furniture and equipment for the room's functionality. (according to document 33 of Supplement 2 of Annex 2.1 of the Terms) | PS
1.2.21. | Metal storage area | - | - | - | - | - | ??? | C | Designed for storing metal sheets, pipes, racks up to 7 t. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 1 room. Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide the necessary furniture and equipment for the room's functionality. (according to document 33 of Supplement 2 of Annex 2.1 of the Terms) | PS
1.3. | Building engineering system rooms |  | 0 | 0 | 0 | 0 | 40
1.5.1. | Technical rooms | - | - | - | - | - | 20 | C | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 1 room. Video surveillance – general monitoring of building access points and entrances, Access control system – not planned.
1.5.2. | Electronic security systems switch room | - | - | - | - | - | 6 | A | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 4 room.
1.5.3. | Switching room (communication distribution point) | - | - | - | - | - | 14 | A
1.4. | Other rooms |  | 0 | 0 | 0 | 0 | 5
1.4.1. | Corridor | - | - | - | - | - | - | C | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 1 room Video surveillance – general monitoring of building access points and entrances, Access control system (including building access) – not planned.
1.4.1. | Cleaning inventory room | - | - | - | - | - | 5 | C
1.5. | Other. Proposed by the Candidate / Participant. | [7 empty] | The Candidate/Participant may supplement their Tender with the solutions that do not contradict the Specifications or are not assessed by the Public Entity (PE)
| Total building area |  | 22 | 0 | 22 | 23 | 4347
The price must match the price of part of the Facility of Supplement 2.1, document 1, worksheet 1
[12 empty] | Total (EUR, excl. VAT) |  |  |  |  | Total cost of the optimisation solutions (EUR excl. VAT). Cost of additional work or savings
REMARKS:
1. The Public Entity fills in the specifications, object data, and design task taking into account the features and purpose of the object.
2. The Public Entity provides known special requirements and descriptions of objects, rooms, spaces, functional blocks, and infrastructure. If descriptions are not provided in the Public Entity tables, the Candidate/Participant must submit their tenders in accordance with applicable regulations, standards, and other legal acts.
3. The Candidate/Participant may propose and suggest possible optimisations in their solutions (by suggesting to supplement the Specifications, justifying the benefits of the proposals and their impact on the price of the Tender).
4. The Public Entity classifies rooms/ spaces/ functional blocks by significance levels into functional sector significance levels A, B, C, and D (Specifications section "Functional sectors").
5. The areas provided in the table are approximate and may change depending on the implementation of regulatory acts and the requirements of the Specifications.
6. The technological rooms must be equipped with an air conditioning system, ensuring the proper operating conditions for the equipment installed in these rooms. Parameters are selected according to the recommendations of computer network equipment manufacturers. Temperature deviations in the rooms must be automatically recorded in the Registration Tool.
7. The size of technological premises indicated in the table is approximate, it is adjusted by evaluating the planned equipment quantities to be installed. The size of the room must allow easy access to the switchgear cabinets and equipment maintenance.
10. Technological rooms should not be located beneath sanitary facilities or in other areas where there is a high risk of flooding.
11. If necessary to clarify the solutions, the Participant may add rows to their table.
12. * The PS must provide for a one-time furniture purchase and warranty maintenance for a period of 5 years
13 The PS must provide equipment/furniture that is mandatory (or necessary) for the proper functioning (use) of buildings/premises, in accordance with legal acts/regulations, the Private Entity’s solutions, etc., including their further technical maintenance throughout the entire Contract period

## 3. Creation of buildings. Needs
Supplement 2.1 document 12 "Technical requirements for the creation of repair workshop"
| Project name |  | Development of a military campus infrastructure in Klaipėda district, Kairiai
| Facility |  | Kairiai military town
| Type of construction |  | New construction
| Annex to terms & conditions |  | Annex 2 Specifications
| Supplement |  | Supplement 2.1 document 12 "Technical requirements for the creation of repair workshop"
| Supplement document (worksheet) |  | worksheet 3. Development of buildings. Needs
| The name of the room/space/functional block | Total number of places | Phones connected to the KATT | Computer networks are connected to the unit's network 2 | Computer networks are connected to the KAS network 1 | Number of computerised workstations | Approximate area (sq. m) (if needed to determine) | The significance level of the room/space/functional block (A, B, C and D) | Description of special requirements for premises/areas (if applicable) | The area of the premises/space/functional block in square metres proposed by the Candidate/Participant | numbering of premises according to the explanations on the drawings proposed by the Candidate/Participant | Cost of development of the solution proposed by the Candidate / Participant (EUR excl. VAT) | Furniture/equipment inventory |  |  |  | Possible optimisation proposed by the Candidate – additional solutions to those in the Specification (reference to the Tender document, section, paragraph, clause). Price (EUR excl. VAT) This section is to be completed only for the Initial Tender | REMARKS
Item No. | [12 empty] | Description of the building's furniture/equipment inventory needs and Special Requirements (if any) | The planned furniture/equipment inventory is purchased by *PS, **PS, or VS | The price of furniture and equipment proposed by the Candidate/Participant for the investor (which is purchased by the Private Entity) (*PS, **PS)) (EUR excl. VAT) | Cost for the installation of the furniture and equipment inventory proposed by the Candidate/Participant (*PS, **PS) (EUR excl. VAT)
| To be completed by the Public entity (PE). When submitting the Tender, the information “To be completed by the Candidate/Participant" may be suspplemented by the Candidate/Participant | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | to be completed by Candidate / Participant | to be completed by Candidate / Participant | to be completed by Candidate / Participant | To be completed by Public entity | To be completed by Public entity | to be completed by Candidate / Participant | to be completed by Candidate / Participant | To be completed by the candidate (only applicable for Initial Tender)
1. | Shed (type 3) (for waste) | [16 empty] | 2 units are designed.
1.1. | Canopies (open) | - | - | - | - | - | 500 | C | Lighting solutions must be provided for the internal space, divided into 100 m² sections. Height to the structure – 4.5 m. The flooring must withstand an axle load of 12 t.
1.2. | Other. Proposed by the Candidate / Participant. | [7 empty] | The Candidate/Participant may supplement their Tender with the solutions that do not contradict the Specifications or are not assessed by the Public Entity (PE)
| Total building area |  | 0 | 0 | 0 | 0 | 500 |  | max 500
The price must match the price of part of the Facility of Supplement 2.1, document 1, worksheet 1
[12 empty] | Total (EUR, excl. VAT) |  |  |  |  | Total cost of the optimisation solutions (EUR excl. VAT). Cost of additional work or savings
REMARKS:
1. The Public Entity fills in the specifications, object data, and design task taking into account the features and purpose of the object.
2. The Public Entity provides known special requirements and descriptions of objects, rooms, spaces, functional blocks, and infrastructure. If descriptions are not provided in the Public Entity tables, the Candidate/Participant must submit their tenders in accordance with applicable regulations, standards, and other legal acts.
3. The Candidate/Participant may propose and suggest possible optimisations in their solutions (by suggesting to supplement the Specifications, justifying the benefits of the proposals and their impact on the price of the Tender).
4. The Public Entity classifies rooms/ spaces/ functional blocks by significance levels into functional sector significance levels A, B, C, and D (Specifications section "Functional sectors").
5. The areas provided in the table are approximate and may change depending on the implementation of regulatory acts and the requirements of the Specifications.
6. The technological rooms must be equipped with an air conditioning system, ensuring the proper operating conditions for the equipment installed in these rooms. Parameters are selected according to the recommendations of computer network equipment manufacturers. Temperature deviations in the rooms must be automatically recorded in the Registration Tool.
7. The size of technological premises indicated in the table is approximate, it is adjusted by evaluating the planned equipment quantities to be installed. The size of the room must allow easy access to the switchgear cabinets and equipment maintenance.
10. Technological rooms should not be located beneath sanitary facilities or in other areas where there is a high risk of flooding.
11. If necessary to clarify the solutions, the Participant may add rows to their table.
12. * The PS must provide for a one-time furniture purchase and warranty maintenance for a period of 5 years
13 **The PS must provide equipment/furniture that is mandatory (or necessary) for the proper functioning (use) of buildings/premises, in accordance with legal acts/regulations, the Private Entity’s solutions, etc., including their further technical maintenance throughout the entire Contract period

## 4. Creation of buildings. Const
Supplement 2.1 document 12 "Technical requirements for the creation of repair workshop"
| Project name | Development of a military campus infrastructure in Klaipėda district, Kairiai
| Facility | Kairiai military town
| Type of construction | New construction
| Annex to terms & conditions | Annex 2 Specifications
| Supplement | Supplement 2.1 document 12 "Technical requirements for the creation of repair workshop"
| Supplement document (worksheet) | worksheet 4. Development of buildings. Construction
Item No. | Building part/ System/ Area | Description of special requirements for premises/areas (if applicable) | Description of solutions proposed by the Candidate/Participant (reference to the annex of the Tender: Section, part, item of the Tender). | Cost of development of the solution proposed by the Candidate / Participant (EUR excl. VAT) | Possible optimisation proposed by the Candidate – additional solutions to those in the Specification (reference to the Tender document, section, paragraph, clause). Price (EUR excl. VAT) This section is to be completed only for the Initial Tender | REMARKS
| To be completed by the Public entity (PE). When submitting the Tender, the information “To be completed by the Candidate/Participant" may be suspplemented by the Candidate/Participant | to be filled by the Public Entity (if specific requirements are known and applied | to be completed by Candidate / Participant | to be completed by Candidate / Participant | To be completed by the candidate (only applicable for Initial Tender)
Repair workshop (type 1)
1. | Building structures and other elements
1.1. | Foundations | 1. Foundations under supporting structures must be designed considering the loads, the nature of the load increase, and the foundation ground properties. 2. The final decision on the type of foundation must be based on the results of engineering geological studies and a cost comparison of different foundation types. The Participant provides information on selected foundation type, including structures, insulation, and finishing materials etc.
1.2. | Plinth installation | Wall covers (by the type of coating) must be compatible with the room purpose, resistant to wet cleaning and, where necessary, to chemicals used for disinfection. The Participant provides information on plinth solutions, finishing materials etc.
1.3. | Load-bearing external walls, structures | 1. For rooms subject to stricter security requirements, the exterior walls must ensure increased security (e.g., for weapons, document storage, and other rooms); 2. The areas designated for soldier movement must be separated from the external building enclosures to protect the building façades and their external elements from accidental damage; 3. If necessary, external wall cladding must be used, ensuring its acoustic properties. Colours and materials must be selected based on resistance to dirt, ease of cleaning, material aging, wear, and simplicity of maintenance. 4. The architecture of the building's facade must be simple (without intricate details); 5. Facades must be easy to maintain and durable, with facade materials offering increased resistance to dirt and damage; The Participant provides information on external wall solutions, including structures, insulation, and finishing layers etc.
1.4. | Non-load-bearing external walls, structures
1.5. | Slabs on the ground. | 1. Acoustic noise in shared areas must not exceed 85 dBA, in work offices and meeting rooms – up to 50 dBA, and in sleeping areas – up to 32 dBA. 2. In special rooms with a high or medium potential for liquid accumulation, a floor slope must be installed to allow liquids to drain into the sewage system. 3. Floor coverings must be suitable for their intended use based on the function of the rooms or spaces where they are installed. 4. The floors must be designed to withstand their own weight and operational loads, considering the intended purpose of the rooms. The participant provides information about the floor slab structure (insulation types, layers) etc.)
1.6. | Floor slabs between levels
1.7. | Roof | 1. Measures to prevent the formation of icicles must be provided; 2. The roof must be easy to maintain, with maintenance walkways and platforms installed. Access to the roof must be easy but restricted with safety measures to prevent unauthorized individuals from accessing it; 3. Water from the building’s roof must be drained in such a way that it does not damage the building’s structure, roads, sidewalks, adjacent buildings, or harm the environment, and is directed into the underground stormwater drainage system. The participant provides information about the roof structure, insulation types and layers, and finishes. Rainwater collection and drainage system, roof protective railings, walkways, protective grilles, snow-retaining grilles, fire escape ladders etc.
1.8. | Load-bearing internal walls | Wall covers (by the type of coating) must be compatible with the room purpose, resistant to wet cleaning and, where necessary, to chemicals used for disinfection. The Participant provides information on internal wall solutions, including structures, insulation, and finishing layers etc.
1.9. | Non-load-bearing internal walls
1.10. | Structural elements | 1. The structure of the buildings must be durable enough to withstand the negative effects of rare and potentially dangerous events. 2. The main criterion when choosing building materials is public safety and material durability. These materials must be used in such a way that they meet the requirements or are of better quality than those specified in the technical requirements of these Specifications. The Participant provides information on stairs, ramps, balconies, and loggia structures, including coatings etc.
1.11. | Partitions | 1. The finishing of partitions can be minimal (for example, where allowed by the construction norms, walls can be left unplastered, painted, or impregnated), but must comply with the intended use of the rooms. 2. Wall covers (by the type of coating) must be compatible with the room purpose, resistant to wet cleaning and, where necessary, to chemicals used for disinfection. The Participant provides information on Partition types, structures, finishes etc.
1.12. | Floor coverings and finishes. | 1. The floors in sanitary rooms/ spaces/ areas must be non-slip, waterproof, easy to clean, resistant to the cleaning agents and disinfectants used, and must have a slope towards the water drainage channels for self-collection into the sewage system. 2. Floor and stair surfaces must be non-slip, easy to clean, and resistant to the chemicals used for wet cleaning and disinfection. The Participant provides information on floor type, structures, finish. The main room groups are distinguished – corridors, halls, administrative rooms, service rooms, and technical auxiliary rooms etc.
1.13. | Wall finish | 1. Design the facades of buildings, considering the purpose of the buildings, the cohesive architectural appearance of the area, and long-term durability. 2. The interior wall finishes can be minimal (for example, where construction regulations allow, walls can be unplastered and painted or impregnated), but they must meet the room's intended use. Walls in building rooms may be impregnated with clear liquids or impregnating paints. 3. The wall covering (according to the type of covering) must match the room’s purpose, be resistant to damp cleaning, and where necessary, resistant to chemicals used for disinfecting. The participant provides descriptions of wall construction types, frame infills, and finishes etc.
1.14. | Ceiling finishing | The ceiling finishing may be minimal, but it must comply with the intended use of the room. The Participant provides information on ceiling types, structures, finishes etc.
1.15. | External doors, windows, and showcases | Where required by special regulations, protective metal grills should be installed, and access to windows from the exterior of the building should be restricted. The Participant provides information on windows, showcases, doors, gates, including sills, trims, fittings, drive mechanisms, micro-ventilation elements, and other installed components.
1.16. | Skylights | The Participant provides information on skylights, roof hatches, including trims, fittings, drive mechanisms, ventilation elements, and other installed components.
1.17. | Internal doors and windows | 1. Internal doors, depending on the purpose, security, and number of operating cycles – metal, plastic, aluminium, or wooden (veneered). Fittings must be adapted to the designated use of the premises; 2. Access control doors must be equipped with electromagnetic locks, scanning devices, and, if required, intercom systems. 3. Doors must be designed to provide sound insulation where required, withstand increased operational loads, and be easy to operate. 4. Access to designated zones must be restricted. (detailed descriptions are provided in Supplement 2 "Specifications for Buildings, Structures, and Territory"). 5. In high-traffic areas, doors must also be protected with galvanised steel plates covering up to half their height. In areas where specific architectural solutions are required for internal equipment, other protective measures may be proposed. Access to doors and movement zones must be protected from damage and accelerated material wear. 6. Information plates must be installed on doors. Information plates must be installed on interior doors and at entrances to each floor’s rooms, allowing for easy modification of displayed information. The information to be specified on the arrows and information boards will be determined by the Public Entity. 7. All internal doors must have locks controlled by keys. There must be a manual method to open the electric skis using a key in case they do not work. The Participant provides information on interior room windows, showcases, doors, gates, including sills, trims, fittings, drive mechanisms, and other installed components.
1.18. | Sun protection | External heat gain management must be planned by selecting equipment (devices) that limit direct sunlight from entering the rooms. They can be controlled mechanically when installed inside or be installed on the exterior of the window (room), in which case their control must be electric. The sun protection measures to be installed must be designed for increased operational load, as well as being easy and simple to maintain, with the ability to limit or even stop direct sunlight, while allowing diffuse light to pass through. The Participant provides information on roller blinds, awnings, and shutters, including drive mechanisms etc.
1.19. | Special built-in elements | Outdoor stair railings, handrails, joints, and covering elements must be installed from stainless steel pipes. Outdoor stair railings, handrails, joints, and covering elements must be made of stainless steel. The Participant provides information on grilles, railings, handrails, decorative and covering elements (light well covers, foot cleaning grates) et al).
1.20. | Other
1.21. | Other. Proposed by the Candidate / Participant. | The Candidate / Participant may add to the Solution / Tender its own solutions that are not in conflict with the Specification or not evaluated by the Public Entity (PE)
2. | Building internal engineering systems
2.1. | Heating systems and equipment | 1. It is necessary to install heat consumption metering. Measuring devices must have a continuous scanning function. The possibility of adapting the heating installation for the functional separation of the military unit facility must be planned, taking into account the ability to normalise the temperature in different areas and rooms of the military unit facility by location and time, as well as the momentary increase or loss of heat, separately measuring heat consumption in separated facilities, and smoothly adjusting parameters to ensure continuous adaptation to demand, including at different times of the day. 2. Areas where underfloor heating will be installed must be planned in such a way that they do not interfere with future furniture attachment. The participant provides a description – heat supply, heating system, heat production, heating pipelines etc. Radiators, underfloor heating, radiant heating systems etc. Metering.
2.2. | Ventilation systems and equipment | 1. Design effective solutions for heating, ventilation, cooling (air conditioning, refrigeration) systems, considering the equipment and tools stored in the storage rooms, ensuring microclimate parameters; 2. In the server rooms and uninterrupted power supply room, a separate automated precision control air conditioning system must be provided. Separate electrical panels must be provided for air conditioning equipment, and a separate grounding loop must be provided for the equipment. A constant temperature of 20–25 °C and relative humidity of 40–55% must be maintained in these rooms. The conditioning system is duplicated: one working and the other backup units. The backup air conditioner must activate automatically by rotating if the temperature in the room increases or in the event of the main air conditioner failure; 3. A separate ventilation system must be provided in the server room and the uninterruptible power supply room; no engineering systems not directly related to these rooms should be installed in these premises. Rooms must be protected from water flooding. The Participant provides information on air supply and extraction units, with or without air treatment functionality, ventilation equipment, technical air system ventilation systems, ducts and pipelines, ventilation openings and grilles, cooling systems, ducts and pipelines.
2.3. | Cooling (air conditioning) systems and equipment | 1. The components of the cooling system must have an anti-condensation insulating layer; 2. Water cooling system distributors (cartridges, air conditioning pipe equipment, brackets) in accessible locations must have regulating and shut-off valves to allow for system operation and control; 3. The system must be connected to the general control system of the military unit; 4. To cool the server rooms, precision-controlled air conditioners must be installed, which operate at low outdoor temperatures, as well as an air supply and exhaust system connected to the building’s control system. 5. It is recommended to assess the possibility of creating the necessary engineering solutions to recover/reuse heat emitted in server rooms. The Participant provides information on selected cooling (air conditioning) system and equipment.
2.4. | Water supply and sewage systems and equipment | 1. It is necessary to install water consumption measurement devices with a remote reading function; 2. To ensure the required water consumption rates and the fire water supply system needs, appropriate equipment must be selected and installed 3. Main water supply pipelines to all Military Unit Objects must have separate meters and distribution. The Participant provides information on water metering etc.
2.5. | Water metering installation | 1. It is necessary to install water consumption measurement devices with a remote reading function; 2. To ensure the required water consumption rates and the fire water supply system needs, appropriate equipment must be selected and installed 3. Main water supply pipelines to all Military Unit Objects must have separate meters and distribution. The Participant provides information on water metering etc.
2.6. | Cold water system | 1. The water supply in the military unit's objects must be designed so that water is supplied to all collection points, taking into account the pressure, flow rate, water properties, and the purpose of the building's use, as well as peak water consumption at the same time. 2. When different requirements are set for the parameters of the water used at the collection points, water can be supplied through independent pipelines or water supply systems, providing water with the required properties from the corresponding external water supply networks or systems, which appropriately prepare the water. Water supply and distribution must be sufficient and meet the requirements of hygiene standards and other legal acts. 3. Water consumption metering devices with remote reading functionality must be installed. 4. Separate metering must be installed for each system with different water consumption purposes. 5. Sanitary equipment must be aesthetic, durable, modern, and suitable for the functional area in which it is installed, and must comply with sanitary requirements. 6. Water must be supplied to the facilities by connecting them to the main water supply network. 7. The equipment must be installed to ensure that the water consumption indicators for the building complex are no less than the standard values and that the fire protection water supply needs are met. 8. If the supplied water quality is insufficient, it must be achieved through appropriate water treatment engineering solutions. The number of drinking water supply points must be determined in accordance with regulations and standards. The Participant provides information on the proposed cold water supply system. |  |  |  | To ensure the longevity of household appliances, the participant recommends supplementing the technical specifications so that water used for laundry and dishwashing equipment is softened
2.7. | Hot water systems and equipment | 1. Wastewater must be collected and directed according to economically/technically justified solutions, issued technical conditions. 2. Toilet pots must have a water barrier inside. Water to toilet cisterns must be supplied silently (quiet operation), using no more than 6 l / 3 l of water for flushing. 3. Urinals must have a contactless tap. 4. In all buildings, except for the barracks washbasins near the WC (or closest to them), contactless taps with temperature limiters must be installed, as well as solutions for legionella prevention or pipe cleaning, preventing stagnant water from forming in the pipes (especially at the furthest points/water taps). In the barracks, one of the four mixers must be contactless. 5. All sanitary devices, drain receivers, faucets, and other plumbing fixtures must be certified. 6. Plumbing appliances installed in the facility must meet the following general requirements: their interior and exterior must have a smooth, easily cleanable surface (all appliances can be made of stainless steel); they must not have sharp protruding parts (in the appliance and in the fixing details); washbasins must be equipped with chrome-plated metal siphons that match the colour of the water mixing taps and faucets; toilet bowls must be equipped with seats and covers made of durable plastic. The participant provides a description – wastewater pipelines, wastewater collection facilities, wastewater treatment facilities Wastewater treatment plants
2.8. | Domestic wastewater systems and equipment | 1. Wastewater must be collected and directed according to economically/technically justified solutions, issued technical conditions. 2. Toilet pots must have a water barrier inside. Water to toilet cisterns must be supplied silently (quiet operation), using no more than 6 l / 3 l of water for flushing. 3. Urinals must have a contactless tap. 4. In all buildings, except for the barracks washbasins near the WC (or closest to them), contactless taps with temperature limiters must be installed, as well as solutions for legionella prevention or pipe cleaning, preventing stagnant water from forming in the pipes (especially at the furthest points/water taps). In the barracks, one of the four mixers must be contactless. 5. All sanitary devices, drain receivers, faucets, and other plumbing fixtures must be certified. 6. Plumbing appliances installed in the facility must meet the following general requirements: their interior and exterior must have a smooth, easily cleanable surface (all appliances can be made of stainless steel); they must not have sharp protruding parts (in the appliance and in the fixing details); washbasins must be equipped with chrome-plated metal siphons that match the colour of the water mixing taps and faucets; toilet bowls must be equipped with seats and covers made of durable plastic. The participant provides a description – wastewater pipelines, wastewater collection facilities, wastewater treatment facilities Wastewater treatment plants |  |  |  | Sections 2.7 and 2.8 are identical and describe sanitary appliances.
2.9. | Surface water drainage, rainwater systems, and devices | Rainwater drainage from the structures must be ensured, collected, and channelled according to the issued sewage network connection conditions. The participant provides a description – wastewater pipelines, wastewater collection facilities, wastewater treatment facilities etc.
2.10. | Plumbing appliances | 1. Sanitary equipment must be aesthetic, durable, modern, and suitable for the functional area in which it is installed, and must comply with sanitary requirements. 2. Sanitary infrastructure must be equipped with soap dispensers, hand dryers, paper towel dispensers, toilet paper dispensers, and automatically switched on and off lights. The Participant provides information on sanitary appliances, equipment, and systems.
2.11. | Other equipment | The Participant provides information on other equipment not included in the listed water supply and wastewater disposal systems.
2.12. | Electrical systems and equipment | 1. Locations and movement paths with few users or where users are not always present must be equipped with occupancy sensors. This is particularly important in storage and inventory areas, as well as in places with low movement. The quality of the equipment and the thoughtful placement of occupancy detectors must ensure complete convenience, as the lights must always turn on and off at the required times. 2. Artificial lighting must be coordinated with surveillance equipment spaces and arranged so as not to dazzle the video surveillance cameras. The private partner must aim to reduce the number of lighting source models used. 3. All equipment must be accessible for cleaning and maintenance, especially in high locations. 4. Outdoor lighting must be controlled from the room. 5. The lighting of auxiliary rooms must be distributed according to functional zones, but the lighting of zones related to event functions must be centralized and controlled from a dedicated room. 6. A sufficient power capacity three-phase power supply must be planned (for all planned equipment). The electrical networks of the buildings must be designed for all types (facades, territories, fire extinguishing equipment, local television networks, fire hydrant light indicators, safety signs, call systems, light enclosures). and others) to power the lighting. Electrical cable installation must comply with the technical requirements for this system’s installation. 7. In the building's premises, all installed control and protection devices must have a label indicating the schematic dependency and purpose. There must be a label with the name of the recipients and the line's purpose in the internal part of the door panel, on the panel by the devices. The Participant provides information on high and/or medium voltage distribution equipment. Electric power generators, including cooling, exhaust gas and fuel supply systems, central battery and uninterruptible power supply equipment, and photovoltaic systems. Cables, wires, secondary distributors, routing systems, installation devices. Fixed lights, including electric lamps. Lightning protection, lightning rod, and grounding systems. Electricity metering.
2.13. | Security alarm systems and devices | The general requirements of the system are described in Supplement 2.1 document 36 "Requirements for Electronic Protection Systems"; The participant must provide information on the security alarm system and equipment.
2.14. | Access control systems and devices. | If card readers are installed outdoors, they must be mechanically sturdy and resistant to atmospheric conditions. In an emergency (power failure), access-controlled doors must be unlockable with a key. The general requirements of the system are described in Suplement 2.1 document 36 "Requirements for Electronic Protection Systems". The Participant provides information on electromagnetic or mechanical locks. Access control system and devices.
2.15. | Video surveillance systems and equipment | The general requirements of the system are described in Suplement 2.1 document 36 "Requirements for Electronic Protection Systems". The Participant provides information on video surveillance cameras, video recording, storage, and display equipment.
2.16. | Telecommunications and communication information transmission systems and equipment | When designing telecommunications and computer networks and installing premises for primary equipment, the Cyber Defence Service of the Lithuanian Armed Forces (LK KGV ITT) must be provided with equipment room layouts, communication cables, networks, switching blocks, workstations, power and grounding system schemes in electronic format. When designing and constructing buildings and installing Equipment for Networks 1 and 2, representatives from the Cyber Defence Service of the Lithuanian Armed Forces (LK KGV ITT) must take part, in addition to other officials. The participant independently selects a communication provider required for PS needs and/or IP TV service provision. VS organizes the connection and service provision of the Ministry of Defence data transmission network. The Participant provides information on purpose of communication network, switch cabinet locations in the building, network switches, accessories, and other equipment.
2.17. | Automation systems and devices | 1. A closed (local) building management system must be installed, allowing both monitoring and control of the main engineering system parameters. 2. The accounting data analysis and processing software must be installed, designed for processing water, heat, electricity, and other meter data, generating reports, data analysis, and forecasting future needs. 3. With the help of the installed systems, it must be possible to monitor and record the main microclimate parameters of at least five typical rooms (spaces). 4. Meter readings must be transmitted automatically. 5. The storage of copies of the transmitted telemetry data must be ensured. The Participant provides information on automated systems, control and monitoring devices, programming devices, sensors and actuators, communication intersection stations, and software for automated stations.
2.18. | Smoke extraction systems and equipment | The smoke extraction system and/or solution must be installed in accordance with the applicable regulations and standards. The Participant provides information on smoke extraction system, ducts, and equipment.
2.19. | Fire systems, fire detection systems, and equipment | The Participant provides information on fire detection and fire alarm systems.
2.20. | Fire extinguishing systems and equipment | 1. The fire water supply system must comply with the applicable standards; 2. The private partner must design an adequate number of external fire-fighting measures, considering the changes in the water supply system and fire safety standards. 3. The private partner, considering the number of users in a specific Military Unit Object, must ensure appropriate evacuation conditions, ensuring that users can quickly and safely leave the danger zone or the area where a fire has occurred. Also, the appropriate structure, dimensions, and other technical fire safety measures must be ensured. The Participant provides information on fire suppression systems and devices.
2.21. | Gas pipeline system and equipment | The participant provides descriptions of systems and equipment, technical parameters, and details of the proposed installed equipment (location in the building, power ratings, specifications, etc.).
2.22. | Specific use devices, other technological devices and systems | The Participant provides information on built-in elements for special purposes, signposts, informational and directional signs, colour-coded guidance systems, air compressors, liquid storage tanks etc.
2.23. | Renewable energy systems and devices are installed in the building. The system and equipment installed in the area are not evaluated here; such information is provided in the "Territory" worksheet before the field of engineering networks and systems. | The participant provides descriptions of systems and equipment, technical parameters, and details of the proposed installed equipment (location in the building, power ratings, specifications, etc.).
2.24. | Other equipment
3. | Other. Proposed by the Candidate / Participant. |  |  |  |  | The Candidate / Participant may add to the Solution / Tender its own solutions that are not in conflict with the Specification or not evaluated by the Public Entity (PE)
The price must match the price of part of the Facility of Supplement 2.1, document 1, worksheet 1
|  |  |  | Total (EUR, excl. VAT) | Total cost of the optimisation solutions (EUR excl. VAT). Cost of additional work or savings
REMARKS:
1. The Public Entity fills in the specifications, object data, and design task taking into account the specific features and purpose of the object part.
2. The Public Entity provides known special requirements and descriptions of objects, rooms, functional blocks, and infrastructure. If descriptions are not provided in the Public Entity tables, the Candidate/Participant must submit their tenders in accordance with applicable regulations, standards, and other legal acts.
3. The Candidate may propose and suggest possible optimisations (by suggesting to supplement the Specifications, justifying the benefits of the proposals and their impact on the price of the Tender).
4. Where possible and rational, the cost of creating a facility or other part of a building should be detailed by isolating individual parts or components of the building and specifying the anticipated cost of each respective part or component.

## 5. Creation of buildings. Const
Supplement 2.1 document 12 "Technical requirements for the creation of repair workshop"
| Project name | Development of a military campus infrastructure in Klaipėda district, Kairiai
| Facility | Kairiai military town
| Type of construction | New construction
| Annex to terms & conditions | Annex 2 Specifications
| Supplement | Supplement 2.1 document 12 "Technical requirements for the creation of repair workshop"
| Supplement document (worksheet) | worksheet 5. Development of buildings. Construction
Item No. | Building part/ System/ Area | Description of special requirements for premises/areas (if applicable) | Description of solutions proposed by the Candidate/Participant (reference to the annex of the Tender: Section, part, item of the Tender). | Cost of development of the solution proposed by the Candidate / Participant (EUR excl. VAT) | Possible optimisation proposed by the Candidate – additional solutions to those in the Specification (reference to the Tender document, section, paragraph, clause). Price (EUR excl. VAT) This section is to be completed only for the Initial Tender | REMARKS
| To be completed by the Public entity (PE). When submitting the Tender, the information “To be completed by the Candidate/Participant" may be suspplemented by the Candidate/Participant | to be filled by the Public Entity (if specific requirements are known and applied | to be completed by Candidate / Participant | to be completed by Candidate / Participant | To be completed by the candidate (only applicable for Initial Tender)
Repair workshop (type 2)
1. | Building structures and other elements
1.1. | Foundations | 1. Foundations under supporting structures must be designed considering the loads, the nature of the load increase, and the foundation ground properties. 2. The final decision on the type of foundation must be based on the results of engineering geological studies and a cost comparison of different foundation types. The Participant provides information on selected foundation type, including structures, insulation, and finishing materials etc.
1.2. | Plinth installation | Wall covers (by the type of coating) must be compatible with the room purpose, resistant to wet cleaning and, where necessary, to chemicals used for disinfection. The Participant provides information on plinth solutions, finishing materials etc.
1.3. | Load-bearing external walls, structures | 1. For rooms subject to stricter security requirements, the exterior walls must ensure increased security (e.g., for weapons, document storage, and other rooms); 2. The areas designated for soldier movement must be separated from the external building enclosures to protect the building façades and their external elements from accidental damage; 3. If necessary, external wall cladding must be used, ensuring its acoustic properties. Colours and materials must be selected based on resistance to dirt, ease of cleaning, material aging, wear, and simplicity of maintenance. 4. The architecture of the building's facade must be simple (without intricate details); 5. Facades must be easy to maintain and durable, with facade materials offering increased resistance to dirt and damage; The Participant provides information on external wall solutions, including structures, insulation, and finishing layers etc.
1.4. | Non-load-bearing external walls, structures
1.5. | Slabs on the ground. | 1. Acoustic noise in shared areas must not exceed 85 dBA, in work offices and meeting rooms – up to 50 dBA, and in sleeping areas – up to 32 dBA. 2. In special rooms with a high or medium potential for liquid accumulation, a floor slope must be installed to allow liquids to drain into the sewage system. 3. Floor coverings must be suitable for their intended use based on the function of the rooms or spaces where they are installed. 4. The floors must be designed to withstand their own weight and operational loads, considering the intended purpose of the rooms. The participant provides information about the floor slab structure (insulation types, layers) etc.)
1.6. | Floor slabs between levels
1.7. | Roof | 1. Measures to prevent the formation of icicles must be provided; 2. The roof must be easy to maintain, with maintenance walkways and platforms installed. Access to the roof must be easy but restricted with safety measures to prevent unauthorized individuals from accessing it; 3. Water from the building’s roof must be drained in such a way that it does not damage the building’s structure, roads, sidewalks, adjacent buildings, or harm the environment, and is directed into the underground stormwater drainage system. The participant provides information about the roof structure, insulation types and layers, and finishes. Rainwater collection and drainage system, roof protective railings, walkways, protective grilles, snow-retaining grilles, fire escape ladders etc.
1.8. | Load-bearing internal walls | Wall covers (by the type of coating) must be compatible with the room purpose, resistant to wet cleaning and, where necessary, to chemicals used for disinfection. The Participant provides information on internal wall solutions, including structures, insulation, and finishing layers etc.
1.9. | Non-load-bearing internal walls
1.10. | Structural elements | 1. The structure of the buildings must be durable enough to withstand the negative effects of rare and potentially dangerous events. 2. The main criterion when choosing building materials is public safety and material durability. These materials must be used in such a way that they meet the requirements or are of better quality than those specified in the technical requirements of these Specifications. The Participant provides information on stairs, ramps, balconies, and loggia structures, including coatings etc.
1.11. | Partitions | 1. The finishing of partitions can be minimal (for example, where allowed by the construction norms, walls can be left unplastered, painted, or impregnated), but must comply with the intended use of the rooms. 2. Wall covers (by the type of coating) must be compatible with the room purpose, resistant to wet cleaning and, where necessary, to chemicals used for disinfection. The Participant provides information on Partition types, structures, finishes etc.
1.12. | Floor coverings and finishes. | 1. The floors in sanitary rooms/ spaces/ areas must be non-slip, waterproof, easy to clean, resistant to the cleaning agents and disinfectants used, and must have a slope towards the water drainage channels for self-collection into the sewage system. 2. Floor and stair surfaces must be non-slip, easy to clean, and resistant to the chemicals used for wet cleaning and disinfection. The Participant provides information on floor type, structures, finish. The main room groups are distinguished – corridors, halls, administrative rooms, service rooms, and technical auxiliary rooms etc.
1.13. | Wall finish | 1. Design the facades of buildings, considering the purpose of the buildings, the cohesive architectural appearance of the area, and long-term durability. 2. The interior wall finishes can be minimal (for example, where construction regulations allow, walls can be unplastered and painted or impregnated), but they must meet the room's intended use. Walls in building rooms may be impregnated with clear liquids or impregnating paints. 3. The wall covering (according to the type of covering) must match the room’s purpose, be resistant to damp cleaning, and where necessary, resistant to chemicals used for disinfecting. The participant provides descriptions of wall construction types, frame infills, and finishes etc.
1.14. | Ceiling finishing | The ceiling finishing may be minimal, but it must comply with the intended use of the room. The Participant provides information on ceiling types, structures, finishes etc.
1.15. | External doors, windows, and showcases | Where required by special regulations, protective metal grills should be installed, and access to windows from the exterior of the building should be restricted. The Participant provides information on windows, showcases, doors, gates, including sills, trims, fittings, drive mechanisms, micro-ventilation elements, and other installed components.
1.16. | Skylights | The Participant provides information on skylights, roof hatches, including trims, fittings, drive mechanisms, ventilation elements, and other installed components.
1.17. | Internal doors and windows | 1. Internal doors, depending on the purpose, security, and number of operating cycles – metal, plastic, aluminium, or wooden (veneered). Fittings must be adapted to the designated use of the premises; 2. Access control doors must be equipped with electromagnetic locks, scanning devices, and, if required, intercom systems. 3. Doors must be designed to provide sound insulation where required, withstand increased operational loads, and be easy to operate. 4. Access to designated zones must be restricted. (detailed descriptions are provided in Supplement 2 "Specifications for Buildings, Structures, and Territory"). 5. In high-traffic areas, doors must also be protected with galvanised steel plates covering up to half their height. In areas where specific architectural solutions are required for internal equipment, other protective measures may be proposed. Access to doors and movement zones must be protected from damage and accelerated material wear. 6. Information plates must be installed on doors. Information plates must be installed on interior doors and at entrances to each floor’s rooms, allowing for easy modification of displayed information. The information to be specified on the arrows and information boards will be determined by the Public Entity. 7. All internal doors must have locks controlled by keys. There must be a manual method to open the electric skis using a key in case they do not work. The Participant provides information on interior room windows, showcases, doors, gates, including sills, trims, fittings, drive mechanisms, and other installed components.
1.18. | Sun protection | External heat gain management must be planned by selecting equipment (devices) that limit direct sunlight from entering the rooms. They can be controlled mechanically when installed inside or be installed on the exterior of the window (room), in which case their control must be electric. The sun protection measures to be installed must be designed for increased operational load, as well as being easy and simple to maintain, with the ability to limit or even stop direct sunlight, while allowing diffuse light to pass through. The Participant provides information on roller blinds, awnings, and shutters, including drive mechanisms etc.
1.19. | Special built-in elements | Outdoor stair railings, handrails, joints, and covering elements must be installed from stainless steel pipes. Outdoor stair railings, handrails, joints, and covering elements must be made of stainless steel. The Participant provides information on grilles, railings, handrails, decorative and covering elements (light well covers, foot cleaning grates) et al).
1.20. | Other
1.21. | Other. Proposed by the Candidate / Participant. | The Candidate / Participant may add to the Solution / Tender its own solutions that are not in conflict with the Specification or not evaluated by the Public Entity (PE)
2. | Building internal engineering systems
2.1. | Heating systems and equipment | 1. It is necessary to install heat consumption metering. Measuring devices must have a continuous scanning function. The possibility of adapting the heating installation for the functional separation of the military unit facility must be planned, taking into account the ability to normalise the temperature in different areas and rooms of the military unit facility by location and time, as well as the momentary increase or loss of heat, separately measuring heat consumption in separated facilities, and smoothly adjusting parameters to ensure continuous adaptation to demand, including at different times of the day. 2. Areas where underfloor heating will be installed must be planned in such a way that they do not interfere with future furniture attachment. The participant provides a description – heat supply, heating system, heat production, heating pipelines etc. Radiators, underfloor heating, radiant heating systems etc. Metering.
2.2. | Ventilation systems and equipment | 1. Design effective solutions for heating, ventilation, cooling (air conditioning, refrigeration) systems, considering the equipment and tools stored in the storage rooms, ensuring microclimate parameters; 2. In the server rooms and uninterrupted power supply room, a separate automated precision control air conditioning system must be provided. Separate electrical panels must be provided for air conditioning equipment, and a separate grounding loop must be provided for the equipment. A constant temperature of 20–25 °C and relative humidity of 40–55% must be maintained in these rooms. The conditioning system is duplicated: one working and the other backup units. The backup air conditioner must activate automatically by rotating if the temperature in the room increases or in the event of the main air conditioner failure; 3. A separate ventilation system must be provided in the server room and the uninterruptible power supply room; no engineering systems not directly related to these rooms should be installed in these premises. Rooms must be protected from water flooding. The Participant provides information on air supply and extraction units, with or without air treatment functionality, ventilation equipment, technical air system ventilation systems, ducts and pipelines, ventilation openings and grilles, cooling systems, ducts and pipelines.
2.3. | Cooling (air conditioning) systems and equipment | 1. The components of the cooling system must have an anti-condensation insulating layer; 2. Water cooling system distributors (cartridges, air conditioning pipe equipment, brackets) in accessible locations must have regulating and shut-off valves to allow for system operation and control; 3. The system must be connected to the general control system of the military unit; 4. To cool the server rooms, precision-controlled air conditioners must be installed, which operate at low outdoor temperatures, as well as an air supply and exhaust system connected to the building’s control system. 5. It is recommended to assess the possibility of creating the necessary engineering solutions to recover/reuse heat emitted in server rooms. The Participant provides information on selected cooling (air conditioning) system and equipment.
2.4. | Water supply and sewage systems and equipment | 1. It is necessary to install water consumption measurement devices with a remote reading function; 2. To ensure the required water consumption rates and the fire water supply system needs, appropriate equipment must be selected and installed 3. Main water supply pipelines to all Military Unit Objects must have separate meters and distribution. The Participant provides information on water metering etc.
2.5. | Water metering installation | 1. It is necessary to install water consumption measurement devices with a remote reading function; 2. To ensure the required water consumption rates and the fire water supply system needs, appropriate equipment must be selected and installed 3. Main water supply pipelines to all Military Unit Objects must have separate meters and distribution. The Participant provides information on water metering etc.
2.6. | Cold water system | 1. The water supply in the military unit's objects must be designed so that water is supplied to all collection points, taking into account the pressure, flow rate, water properties, and the purpose of the building's use, as well as peak water consumption at the same time. 2. When different requirements are set for the parameters of the water used at the collection points, water can be supplied through independent pipelines or water supply systems, providing water with the required properties from the corresponding external water supply networks or systems, which appropriately prepare the water. Water supply and distribution must be sufficient and meet the requirements of hygiene standards and other legal acts. 3. Water consumption metering devices with remote reading functionality must be installed. 4. Separate metering must be installed for each system with different water consumption purposes. 5. Sanitary equipment must be aesthetic, durable, modern, and suitable for the functional area in which it is installed, and must comply with sanitary requirements. 6. Water must be supplied to the facilities by connecting them to the main water supply network. 7. The equipment must be installed to ensure that the water consumption indicators for the building complex are no less than the standard values and that the fire protection water supply needs are met. 8. If the supplied water quality is insufficient, it must be achieved through appropriate water treatment engineering solutions. The number of drinking water supply points must be determined in accordance with regulations and standards. The Participant provides information on the proposed cold water supply system.
2.7. | Hot water systems and equipment | 1. Wastewater must be collected and directed according to economically/technically justified solutions, issued technical conditions. 2. Toilet pots must have a water barrier inside. Water to toilet cisterns must be supplied silently (quiet operation), using no more than 6 l / 3 l of water for flushing. 3. Urinals must have a contactless tap. 4. In all buildings, except for the barracks washbasins near the WC (or closest to them), contactless taps with temperature limiters must be installed, as well as solutions for legionella prevention or pipe cleaning, preventing stagnant water from forming in the pipes (especially at the furthest points/water taps). In the barracks, one of the four mixers must be contactless. 5. All sanitary devices, drain receivers, faucets, and other plumbing fixtures must be certified according to the ISO 9000 series or equivalent standard and meet the sizes specified by EN standards, with CE marking. 6. Plumbing appliances installed in the facility must meet the following general requirements: their interior and exterior must have a smooth, easily cleanable surface (all appliances can be made of stainless steel); they must not have sharp protruding parts (in the appliance and in the fixing details); washbasins must be equipped with chrome-plated metal siphons that match the colour of the water mixing taps and faucets; toilet bowls must be equipped with seats and covers made of durable plastic. The participant provides a description – wastewater pipelines, wastewater collection facilities, wastewater treatment facilities Wastewater treatment plants
2.8. | Domestic wastewater systems and equipment | 1. Wastewater must be collected and directed according to economically/technically justified solutions, issued technical conditions. 2. Toilet pots must have a water barrier inside. Water to toilet cisterns must be supplied silently (quiet operation), using no more than 6 l / 3 l of water for flushing. 3. Urinals must have a contactless tap. 4. In all buildings, except for the barracks washbasins near the WC (or closest to them), contactless taps with temperature limiters must be installed, as well as solutions for legionella prevention or pipe cleaning, preventing stagnant water from forming in the pipes (especially at the furthest points/water taps). In the barracks, one of the four mixers must be contactless. 5. All sanitary devices, drain receivers, faucets, and other plumbing fixtures must be certified according to the ISO 9000 series or equivalent standard and meet the sizes specified by EN standards, with CE marking. 6. Plumbing appliances installed in the facility must meet the following general requirements: their interior and exterior must have a smooth, easily cleanable surface (all appliances can be made of stainless steel); they must not have sharp protruding parts (in the appliance and in the fixing details); washbasins must be equipped with chrome-plated metal siphons that match the colour of the water mixing taps and faucets; toilet bowls must be equipped with seats and covers made of durable plastic. The participant provides a description – wastewater pipelines, wastewater collection facilities, wastewater treatment facilities Wastewater treatment plants
2.9. | Surface water drainage, rainwater systems, and devices | Rainwater drainage from the structures must be ensured, collected, and channelled according to the issued sewage network connection conditions. The participant provides a description – wastewater pipelines, wastewater collection facilities, wastewater treatment facilities etc.
2.10. | Plumbing appliances | 1. Sanitary equipment must be aesthetic, durable, modern, and suitable for the functional area in which it is installed, and must comply with sanitary requirements. 2. Sanitary infrastructure must be equipped with soap dispensers, hand dryers, paper towel dispensers, toilet paper dispensers, and automatically switched on and off lights. The Participant provides information on sanitary appliances, equipment, and systems.
2.11. | Other equipment | The Participant provides information on other equipment not included in the listed water supply and wastewater disposal systems.
2.12. | Electrical systems and equipment | 1. Locations and movement paths with few users or where users are not always present must be equipped with occupancy sensors. This is particularly important in storage and inventory areas, as well as in places with low movement. The quality of the equipment and the thoughtful placement of occupancy detectors must ensure complete convenience, as the lights must always turn on and off at the required times. 2. Artificial lighting must be coordinated with surveillance equipment spaces and arranged so as not to dazzle the video surveillance cameras. The private partner must aim to reduce the number of lighting source models used. 3. All equipment must be accessible for cleaning and maintenance, especially in high locations. 4. Outdoor lighting must be controlled from the room. 5. The lighting of auxiliary rooms must be distributed according to functional zones, but the lighting of zones related to event functions must be centralized and controlled from a dedicated room. 6. A sufficient power capacity three-phase power supply must be planned (for all planned equipment). The electrical networks of the buildings must be designed for all types (facades, territories, fire extinguishing equipment, local television networks, fire hydrant light indicators, safety signs, call systems, light enclosures). and others) to power the lighting. Electrical cable installation must comply with the technical requirements for this system’s installation. 7. In the building's premises, all installed control and protection devices must have a label indicating the schematic dependency and purpose. There must be a label with the name of the recipients and the line's purpose in the internal part of the door panel, on the panel by the devices. The Participant provides information on high and/or medium voltage distribution equipment. Electric power generators, including cooling, exhaust gas and fuel supply systems, central battery and uninterruptible power supply equipment, and photovoltaic systems. Cables, wires, secondary distributors, routing systems, installation devices. Fixed lights, including electric lamps. Lightning protection, lightning rod, and grounding systems. Electricity metering.
2.13. | Security alarm systems and devices | The general requirements of the system are described in Supplement 2.1 document 36 "Requirements for Electronic Protection Systems"; The participant must provide information on the security alarm system and equipment.
2.14. | Access control systems and devices. | If card readers are installed outdoors, they must be mechanically sturdy and resistant to atmospheric conditions. In an emergency (power failure), control-operated doors must be unlockable with a key. The general requirements of the system are described in Suplement 2.1 document 36 "Requirements for Electronic Protection Systems". The Participant provides information on electromagnetic or mechanical locks. Access control system and devices.
2.15. | Video surveillance systems and equipment | The general requirements of the system are described in Suplement 2.1 document 36 "Requirements for Electronic Protection Systems". The Participant provides information on video surveillance cameras, video recording, storage, and display equipment.
2.16. | Telecommunications and communication information transmission systems and equipment | When designing telecommunications and computer networks and installing premises for primary equipment, the Cyber Defence Service of the Lithuanian Armed Forces (LK KGV ITT) must be provided with equipment room layouts, communication cables, networks, switching blocks, workstations, power and grounding system schemes in electronic format. When designing and constructing buildings and installing Equipment for Networks 1 and 2, representatives from the Cyber Defence Service of the Lithuanian Armed Forces (LK KGV ITT) must take part, in addition to other officials. The participant independently selects a communication provider required for PS needs and/or IP TV service provision. VS organizes the connection and service provision of the Ministry of Defence data transmission network. The Participant provides information on purpose of communication network, switch cabinet locations in the building, network switches, accessories, and other equipment.
2.17. | Automation systems and devices | 1. A closed (local) building management system must be installed, allowing both monitoring and control of the main engineering system parameters. 2. The accounting data analysis and processing software must be installed, designed for processing water, heat, electricity, and other meter data, generating reports, data analysis, and forecasting future needs. 3. With the help of the installed systems, it must be possible to monitor and record the main microclimate parameters of at least five typical rooms (spaces). 4. Meter readings must be transmitted automatically. 5. The storage of copies of the transmitted telemetry data must be ensured. The Participant provides information on automated systems, control and monitoring devices, programming devices, sensors and actuators, communication intersection stations, and software for automated stations.
2.18. | Smoke extraction systems and equipment | The smoke extraction system and/or solution must be installed in accordance with the applicable regulations and standards. The Participant provides information on smoke extraction system, ducts, and equipment.
2.19. | Fire systems, fire detection systems, and equipment | The Participant provides information on fire detection and fire alarm systems.
2.20. | Fire extinguishing systems and equipment | 1. The fire water supply system must comply with the applicable standards; 2. The private partner must design an adequate number of external fire-fighting measures, considering the changes in the water supply system and fire safety standards. 3. The private partner, considering the number of users in a specific Military Unit Object, must ensure appropriate evacuation conditions, ensuring that users can quickly and safely leave the danger zone or the area where a fire has occurred. Also, the appropriate structure, dimensions, and other technical fire safety measures must be ensured. The Participant provides information on fire suppression systems and devices.
2.21. | Gas pipeline system and equipment | The participant provides descriptions of systems and equipment, technical parameters, and details of the proposed installed equipment (location in the building, power ratings, specifications, etc.).
2.22. | Specific use devices, other technological devices and systems | The Participant provides information on built-in elements for special purposes, signposts, informational and directional signs, colour-coded guidance systems, air compressors, liquid storage tanks etc.
2.23. | Renewable energy systems and devices are installed in the building. The system and equipment installed in the area are not evaluated here; such information is provided in the "Territory" worksheet before the field of engineering networks and systems. | The participant provides descriptions of systems and equipment, technical parameters, and details of the proposed installed equipment (location in the building, power ratings, specifications, etc.).
2.24. | Other equipment
3. | Other. Proposed by the Candidate / Participant. |  |  |  |  | The Candidate / Participant may add to the Solution / Tender its own solutions that are not in conflict with the Specification or not evaluated by the Public Entity (PE)
The price must match the price of part of the Facility of Supplement 2.1, document 1, worksheet 1
|  |  |  | Total (EUR, excl. VAT) | Total cost of the optimisation solutions (EUR excl. VAT). Cost of additional work or savings
REMARKS:
1. The Public Entity fills in the specifications, object data, and design task taking into account the specific features and purpose of the object part.
2. The Public Entity provides known special requirements and descriptions of objects, rooms, functional blocks, and infrastructure. If descriptions are not provided in the Public Entity tables, the Candidate/Participant must submit their tenders in accordance with applicable regulations, standards, and other legal acts.
3. The Candidate may propose and suggest possible optimisations (by suggesting to supplement the Specifications, justifying the benefits of the proposals and their impact on the price of the Tender).
4. Where possible and rational, the cost of creating a facility or other part of a building should be detailed by isolating individual parts or components of the building and specifying the anticipated cost of each respective part or component.

## 6. Creation of buildings. Const
Supplement 2.1 document 12 "Technical requirements for the creation of repair workshop"
| Project name | Development of a military campus infrastructure in Klaipėda district, Kairiai
| Facility | Kairiai military town
| Type of construction | New construction
| Annex to terms & conditions | Annex 2 Specifications
| Supplement | Supplement 2.1 document 12 "Technical requirements for the creation of repair workshop"
| Supplement document (worksheet) | worksheet 6. Development of buildings. Construction
Item No. | Building part/ System/ Area | Description of special requirements for premises/areas (if applicable) | Description of solutions proposed by the Candidate/Participant (reference to the annex of the Tender: Section, part, item of the Tender). | Cost of development of the solution proposed by the Candidate / Participant (EUR excl. VAT) | Possible optimisation proposed by the Candidate – additional solutions to those in the Specification (reference to the Tender document, section, paragraph, clause). Price (EUR excl. VAT) This section is to be completed only for the Initial Tender | REMARKS
| To be completed by the Public entity (PE). When submitting the Tender, the information “To be completed by the Candidate/Participant" may be suspplemented by the Candidate/Participant | to be filled by the Public Entity (if specific requirements are known and applied | to be completed by Candidate / Participant | to be completed by Candidate / Participant | To be completed by the candidate (only applicable for Initial Tender)
| Canopy (type 3) |  |  |  |  | 2 units are designed.
1. | Building structures and other elements
1.1. | Foundations | Foundations under supporting structures must be designed considering the loads, the nature of the load increase, and the foundation ground properties. The solution on the type of foundation must be based on the results of engineering geological studies and a comparison of the costs of different foundation types. The Participant provides information on selected foundation type, including structures, insulation, and finishing materials etc.
1.2. | Non-load-bearing external walls, structures | 1. The architecture of the building's facade must be simple (without intricate details). 2. Facades must be easy to maintain and durable, with facade materials offering increased resistance to dirt and damage. 3. Facade materials must be resistant to adverse climatic effects and urban pollution and/or biological materials (moss, mould, insects, rodents, bird droppings) et al). 4. Taking into account the truck with container scheme below, sufficient distance must be provided for container unloading and vehicle manoeuvring (from the loading façade of the designed building to the façades of adjacent and designed buildings). The Participant provides information on external wall solutions, including structures, insulation, and finishing layers etc.
1.3. | Slabs on the ground. | The participant provides information about the floor slab structure (insulation types, layers) etc.)
1.4. | Roof | 1. Measures to prevent the formation of icicles must be provided; 2. Water from the building’s roof must be drained in such a way that it does not damage the building’s structure, roads, sidewalks, adjacent buildings, or harm the environment, and is directed into the underground stormwater drainage system. The participant provides information about the roof structure, insulation types and layers, and finishes. Rainwater collection and drainage system, roof protective railings, walkways, protective grilles, snow-retaining grilles etc.
1.5. | Structural elements | 1. The structure of the buildings must be durable enough to withstand the negative effects of rare and potentially dangerous events. These materials must be used in such a way that they meet the requirements or are of better quality than those specified in the technical requirements of these Specifications. 2. The maximum distance between the axles of the load-bearing columns of the building must be –< 12.0 m; The Participant provides information on stairs, ramps, balconies, and loggia structures, including coatings etc.
1.5. | Floor coverings and finishes. | 1. The shed's flooring must be rationally designed – a monolithic concrete surface reinforced with polypropylene fibre filler, calculated (by modelling structural loads) to withstand a minimum design axle load of 12.0 t (from wheeled machinery with up to four axles). The floor slopes must direct drainage towards the exterior of the structure – no less than 2% The Participant provides information on floor type, structures, finish etc.
1.6. | Wall finish | The wall finish may be minimal, in accordance with the intended use of the building. The participant provides descriptions of wall construction types, frame infills, and finishes etc.
1.7. | Other | In the most hazardous container movement areas, protective structures (made of sufficiently thick metal pipe constructions) for the canopy structures and systems must be provided, painted in bright warning colours;
1.9. | Other. Proposed by the Candidate / Participant. | The Candidate / Participant may add to the Solution / Tender its own solutions that are not in conflict with the Specification or not evaluated by the Public Entity (PE)
2. | Building interior engineering systems
2.1. | Surface water drainage, rainwater systems, and devices | The canopy installation solution must include solutions for rainwater collection from the roof and other surface water collection and diversion. The participant provides a description – wastewater pipelines, wastewater collection facilities, wastewater treatment facilities etc.
2.2. | Electrical systems and equipment | 1. Lighting solutions must be provided for the canopy’s covered area. Provide two-position interior lighting for the canopy. 20 lx and 100 lx; 2. Provide lighting for the canopy area (at least 20 lx, at least 15 m from the canopy).
2.3. | Video surveillance systems and equipment | The Participant provides information on video surveillance cameras, video recording, storage, and display devices.
2.4. | Fire extinguishing systems and equipment | Provide the installation of fire detection in the canopy, with the signal routed to the Guard post.
2.5. | Other equipment
3. | Other. Proposed by the Candidate / Participant. | The Candidate / Participant may add to the Solution / Tender its own solutions that are not in conflict with the Specification or not evaluated by the Public Entity (PE)
The price must match the price of part of the Facility of Supplement 2.1, document 1, worksheet 1
|  |  |  | Total (EUR, excl. VAT) | Total cost of the optimisation solutions (EUR excl. VAT). Cost of additional work or savings
REMARKS:
1. The Public Entity fills in the specifications, object data, and design task taking into account the specific features and purpose of the object part.
2. The Public Entity provides known special requirements and descriptions of objects, rooms, functional blocks, and infrastructure. If descriptions are not provided in the Public Entity tables, the Candidate/Participant must submit their tenders in accordance with applicable regulations, standards, and other legal acts.
3. The Candidate may propose and suggest possible optimisations (by suggesting to supplement the Specifications, justifying the benefits of the proposals and their impact on the price of the Tender).
4. Where possible and rational, the cost of creating a facility or other part of a building should be detailed by isolating individual parts or components of the building and specifying the anticipated cost of each respective part or component.