## 1. Creation of buildings. Needs
Supplement 2.1 document 3 "Technical requirements for the creation of headquarters"
| Project name |  | Development of a military campus infrastructure in Klaipėda district, Kairiai
| Facility |  | Kairiai military town
| Type of construction |  | New construction
| Annex to terms & conditions |  | Annex 2 Specifications
| Supplement |  | Supplement 2.1 document 3 "Technical requirements for the creation of headquarters"
| Supplement document (worksheet) |  | worksheet 1. Development of buildings. Needs
| The name of the room/space/functional block | Number of places | Phones connected to the KATT | Computer networks are connected to the unit's network 2 | Computer networks are connected to the KAS network 1 | Number of computerised workstations | Approximate area (sq. m) (if needed to determine) | The significance level of the room/space/functional block (A, B, C and D) | Description of special requirements for premises/areas (if applicable) | The area of the premises/space/functional block in square metres proposed by the Candidate/Participant | numbering of premises according to the explanations on the drawings proposed by the Candidate/Participant | Cost of development of the solution proposed by the Candidate / Participant (EUR excl. VAT) | Furniture/equipment inventory |  |  |  | Possible optimisation proposed by the Candidate – additional solutions to those in the Specification (reference to the Tender document, section, paragraph, clause). Price (EUR excl. VAT) This section is to be completed only for the Initial Tender | REMARKS
Item No. | [12 empty] | Description of the building's furniture/equipment inventory needs and Special Requirements (if any) | The planned furniture/equipment inventory is purchased by *PS, **PS, or VS | The price of furniture and equipment proposed by the Candidate/Participant for the investor (which is purchased by the Private Entity) (*PS, **PS)) (EUR excl. VAT) | Cost for the installation of the furniture and equipment inventory proposed by the Candidate/Participant (*PS, **PS) (EUR excl. VAT)
| To be completed by the Public entity (PE). When submitting the Tender, the information “To be completed by the Candidate/Participant" may be suspplemented by the Candidate/Participant | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | to be completed by Candidate / Participant | to be completed by Candidate / Participant | to be completed by Candidate / Participant | To be completed by Public entity | To be completed by Public entity | to be completed by Candidate / Participant | to be completed by Candidate / Participant | To be completed by the candidate (only applicable for Initial Tender)
Headquarters (Type I)
1. | Administrative area | 157 | 50 | 17 | 57 | 74 | 646
1.1. | Office | 1 | 2 | - | 2 | 2 | 18 | B | The installation of technological rooms in Network 1 and access to these rooms are regulated by the Order by the Minister of National Defence of the Republic of Lithuania, dated 10 August 2015, No. V-809) (or other current version of the relevant legal acts in force during the formation or execution of the Contract, or the version of the order replacing this order). When setting up computer workstations and laying computer cables, it must be ensured that cable lengths do not exceed 90 m. The entire building must be supplied with electrical power, with a fully automatic backup switches (full automatic control). The entire building must be provided with backup power using a backup power source (generator). The walls and ceilings must be built of brick, blocks, or constructed from metal sheets, solid wood, or similar materials providing equivalent resistance to break-ins. A location for a safe must be assessed. (400x300x300 mm). The door leaf and frame must be made of metal sheets less than 2 mm thick, solid wood, particleboard, plywood, glass, or similar materials ensuring equivalent resistance to burglary; the door must be fitted with a single lock with a cylindrical core or a lever lock. Window frames must be made of durable material, and the glass must be coated with a protective film. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide spaces for office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.2. | Office | 1 | 1 | - | 1 | 1 | 12 | B |  |  |  |  | Provide spaces for office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.3. | Office | 1 | 2 | - | 2 | 2 | 12 | B |  |  |  |  | Provide spaces for office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.4. | Office | 1 | 1 | - | 1 | 1 | 16 | B |  |  |  |  | Provide spaces for office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.5. | Office | 1 | 1 | - | 1 | 1 | 8 | B |  |  |  |  | Provide spaces for office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.6. | Office | 1 | 1 | - | 1 | 1 | 8 | B |  |  |  |  | Provide spaces for office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.7. | Office | 1 | 1 | - | 1 | 1 | 12 | B |  |  |  |  | Provide spaces for office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.8. | Office | 2 | 1 | - | 2 | 2 | 16 | B |  |  |  |  | Provide spaces for office furniture sets No. 2 and No. 3 (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.9. | Office | 4 | 4 | - | 4 | 4 | 30 | A |  |  |  |  | Provide spaces for office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.10. | Office | 2 | 1 | - | 2 | 2 | 12 | B |  |  |  |  | Provide spaces for office furniture sets No. 2 and No. 3 (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.11. | Office | 2 | 2 | 2 | 2 | 4 | 12 | A | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the Installation of Electronic Security Systems," classified as a Type 4 facility. The premises must be constructed in accordance with the requirements of Resolution No. 820 requirements. |  |  |  | Provide spaces for office furniture sets No. 2 and No. 3 (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.12. | Office | 2 | 2 | - | 1 | 2 | 16 | B | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide spaces for office furniture sets No. 2 and No. 3 (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.13. | Office | 4 | 4 | 4 | 4 | 4 | 24 | B | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the Installation of Electronic Security Systems," classified as a Type 4 facility. The rooms are arranged according to the resolution of the Government of the Republic of Lithuania dated 2018-08-13 No. 820 requirements. |  |  |  | Provide spaces for office furniture sets No. 2 – (1 pcs) and No. 3 – (3 pcs) (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.14. | Office | 1 | 1 | - | 1 | 1 | 12 | B | The installation of technological rooms in Network 1 and access to these rooms are regulated by the Order by the Minister of National Defence of the Republic of Lithuania, dated 10 August 2015, No. V-809) (or other current version of the relevant legal acts in force during the formation or execution of the Contract, or the version of the order replacing this order). When setting up computer workstations and laying computer cables, it must be ensured that cable lengths do not exceed 90 m. The entire building must be supplied with electrical power, with a fully automatic backup switches (full automatic control). The entire building must be provided with backup power using a backup power source (generator). The walls and ceilings must be built of brick, blocks, or constructed from metal sheets, solid wood, or similar materials providing equivalent resistance to break-ins. A location for a safe must be assessed. (400x300x300 mm). The door leaf and frame must be made of metal sheets less than 2 mm thick, solid wood, particleboard, plywood, glass, or similar materials ensuring equivalent resistance to burglary; the door must be fitted with a single lock with a cylindrical core or a lever lock. Window frames must be made of durable material, and the glass must be coated with a protective film. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide spaces for office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.15. | Office | 3 | 3 | - | 3 | 3 | 24 | B |  |  |  |  | Provide spaces for office furniture sets No. 2 – (1 pcs) and No. 3 – (2 pcs) (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.16. | Office | 3 | 3 | - | 3 | 3 | 24 | B |  |  |  |  | Provide spaces for office furniture sets No. 2 – (1 pcs) and No. 3 – (2 pcs) (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.17. | Office | 1 | 1 | - | 1 | 1 | 12 | B |  |  |  |  | Provide spaces for office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.18. | Office | 3 | 3 | - | 3 | 3 | 24 | B |  |  |  |  | Provide spaces for office furniture sets No. 2 – (1 pcs) and No. 3 – (2 pcs) (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.19. | Office | 3 | 3 | - | 3 | 3 | 24 | B |  |  |  |  | Provide spaces for office furniture sets No. 2 – (1 pcs) and No. 3 – (2 pcs) (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.20. | Office | 2 | 2 | - | 1 | 2 | 12 | B |  |  |  |  | Provide spaces for office furniture sets No. 2 and No. 3 (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.21. | Office | 3 | 3 | - | 3 | 3 | 24 | B |  |  |  |  | Provide spaces for office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.22. | Office | 3 | 3 | - | 3 | 3 | 24 | B |  |  |  |  | Provide spaces for office furniture sets No. 2 – (1 pcs) and No. 3 – (2 pcs) (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.23. | Office | 1 | 1 | - | 1 | 1 | 8 | B |  |  |  |  | Provide spaces for office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.24. | Office | 1 | 1 | - | 1 | 1 | 8 | B |  |  |  |  | Provide spaces for office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.25. | Meeting room | 30 | 1 | - | 10 | 10 | 50 | A | of the Government of the Republic of Lithuania of 13 August 2018, No. 820, Sections 44–45, for the meeting room (including pipe inserts, etc.). Lockers for mobile phone storage must be installed at the entrances to meeting rooms. These lockers must be wall-mounted. Each locker must accommodate 20 mobile phones, with the ability to lock each phone individually, and a minimum compartment size of 210×210×210 mm. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 4 room. |  |  |  | Provide a meeting room set No. 6 (according to document 28 of Supplement 2 of Annex 2 of the Terms) (2 pcs) | *PS
1.26. | Storage room | - | - | - | - | - | 20 | C | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 1 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide racks (according to document 26 of Annex 2 Supplement 2.1 of the Terms). | *PS
1.27. | Document storage room | - | - | - | - | - | 8 | B | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide all required equipment and furniture required for the room's functionality. | *PS
1.28. | Document processing room. | 4 | 1 | 6 | - | 6 | 36 | B | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide space for office furniture set No. 2 (4 units). | *PS
1.29. | Meeting hall | 30 | 1 | 5 | - | 7 | 60 | B | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 1 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide a meeting room set No. 6 (according to document 28 of Annex 2 Supplement 2 of the Terms) | *PS
1.30. | Recreation room | 1 | - | - | - | - | 20 | C | The room must include a utility space (a sink with hot and cold water connections, disposable towel and detergent dispensers, kitchen cabinets – 2 units, additional installation of 4 electrical outlets, space for a refrigerator). The refrigerator is purchased by the VS. Magnetic contacts for protective alarms are to be installed on the window sashes and assigned to the high corridor area. |  |  |  | Recreation furniture set (according to document 28 of Supplement 2 of Annex 2 of the Terms) | *PS
1.31. | Sanitary unit rooms with showers, toilets, and washbasins | 30 | - | - | - | - | 40 | C | Magnetic security alarm contacts must be installed on the operable parts of exterior windows and assigned to the high corridor area |  |  |  | Provide all required equipment and furniture required for the room's functionality. | PS
1.32. | Sanitary unit rooms with showers, toilets, and washbasins | 15 | - | - | - | - | 20 | C | The premises must be designed as the primary (central) monitoring and control space of the military unit, |  |  |  | Provide all required equipment and furniture required for the room's functionality. | PS
2. | Special-purpose room zone: | 67 | 3 | 0 | 6 | 6 | 100
2.1. | On-duty room | 2 | 1 | - | 2 | 2 | 20 | A | allowing personnel on duty to monitor and manage the status and functions of all security, fire protection, and other systems within the military unit . Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Remote workstations for the EAS system |  |  |  | Office furniture set No. 3 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | *PS
2.2. | Weapons storage room | 60 | 0 | - | 1 | 1 | 20 | A | The premises must be set up following the order of the Minister of National Defence of the Republic of Lithuania dated 26 March 2009. No. V -254 (or other relevant current versions of the legal acts in force during the formation or execution of the Contract, or the versions of orders replacing these orders). The weapons storage room is recommended to be designed based on the Barracks Planning Norms, approved by the Minister of National Defence on 1 August 2000. No. 875. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 3 room. Access control system – not planned. |  |  |  | The room must be designed and equipped with 5 units of weapon racks (according to document 20 of Annex 2 Supplement 2 of the Terms). The room must include space for 2 safes intended for storing ammunition (according to document 25 of Annex 2 Supplement 2 of the Terms). | *PS
2.3. | Archive room | 1 | 1 | - | 1 | 1 | 20 | A | To optimise the use of allocated space, cabinets must be designed and installed according to the order of the Chief Archivist of Lithuania, dated 28 December 2011, No. V -157 “On the Approval of Document Storage Rules.” Mobile archival shelving, lockable metal safes/cabinets must be installed for document storage. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of access to the building and building entrance, Access control system – not provided. |  |  |  | Provide racks (according to document 26 of Annex 2 Supplement 2.1 of the Terms). | *PS
2.4. | Server room 1/2 | 2 | 1 | - | 2 | 2 | 16 | A | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 4 room.
2.5. | Electronic security system communication room (server room) | 1 | - | - | - | - | 8 | A | Must be located near the security office Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 4 room.
2.6. | Telecommunications equipment room | 1 | - | - | - | - | 8 | A | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 4 room.
2.7. | Communication entry room (hardware) | - | - | - | - | - | 8 | A
2.9. | Building engineering system rooms | 0 | 0 | 0 | 0 | 0 | 26
2.10. | Technical rooms | - | - | - | - | - | 10 | C | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 1 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned.
2.11. | Electronic security systems switch room | - | - | - | - | - | 6 | A | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 4 room.
2.12. | Switching room (communication distribution point) | - | - | - | - | - | 10 | A
3. | Other rooms: | 0 | 0 | 0 | 0 | 0 | 126
3.1. | Corridor | - | - | - | - | - | 120 | C | At the main entrance to the building (inside the building), solutions for washing soldiers' feet (shoes) upon returning from activities must be provided. At each entrance to the building, 15 foot (shoe) washing tubs must be provided. The foot washing area must have a water supply, a solution for washing feet (shoes), and a solution for collecting and removing the residual water during and after washing. Corridors must have designated space for the drinking water inlet and space for the installation of electrical networks for a coffee/snack machine. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 1 room, Video surveillance – general monitoring of access to the building and building entrances inside the corridor, Access control system – Access must be provided at all exterior entrance doors to the building, allowing personnel direct access to the security office control window (further access to the corridor is controlled by access control). An intelligent key issuance cabinet must be installed next to the security office (300 key slots and 10 compartments for key bundles). A certified stationary breathalyser with facial recognition must be installed next to the security office.
3.2. | Cleaning inventory storage room (on each floor) | - | - | - | - | - | 6 | C | Each floor of the building must include technical rooms for storing cleaning equipment. Forced air extraction must be ensured in these rooms, with a sink equipped with hot and cold water connections, and holders must be provided for convenient storage of brushes and other tools.
4. | Other. Proposed by the Candidate / Participant. | [7 empty] | The Candidate/Participant may supplement their Tender with the solutions that do not contradict the Specifications or are not assessed by the Public Entity (PE)
| Total building area | [5 empty] | 898
The price must match the price of part of the Facility of Supplement 2.1, document 1, worksheet 1
[12 empty] | Total (EUR, excl. VAT) |  |  |  |  | Total cost of the optimisation solutions (EUR excl. VAT). Cost of additional work or savings
REMARKS:
1. The Public Entity fills in the specifications, object data, and design task taking into account the features and purpose of the object.
2. The Public Entity provides known special requirements and descriptions of objects, rooms, spaces, functional blocks, and infrastructure. If descriptions are not provided in the Public Entity tables, the Candidate/Participant must submit their tenders in accordance with applicable regulations, standards, and other legal acts.
3. The Candidate/Participant may propose and suggest possible optimisations in their solutions (by suggesting to supplement the Specifications, justifying the benefits of the proposals and their impact on the price of the Tender).
4. The Public Entity classifies rooms/ spaces/ functional blocks by significance levels into functional sector significance levels A, B, C, and D (Specifications section "Functional sectors").
5. The areas provided in the table are approximate and may change depending on the implementation of regulatory acts and the requirements of the Specifications.
6. The technological rooms must be equipped with an air conditioning system, ensuring the proper operating conditions for the equipment installed in these rooms. Parameters are selected according to the recommendations of computer network equipment manufacturers. Temperature deviations in the rooms must be automatically recorded in the Registration Tool.
7. The size of technological premises indicated in the table is approximate, it is adjusted by evaluating the planned equipment quantities to be installed. The size of the room must allow easy access to the switchgear cabinets and equipment maintenance.
10. Technological rooms should not be located beneath sanitary facilities or in other areas where there is a high risk of flooding.
11. If necessary to clarify the solutions, the Participant may add rows to their table.
12. * The PS must provide for a one-time furniture purchase and warranty maintenance for a period of 5 years
13 The PS must provide equipment/furniture that is mandatory (or necessary) for the proper functioning (use) of buildings/premises, in accordance with legal acts/regulations, the Private Entity’s solutions, etc., including their further technical maintenance throughout the entire Contract period
14. VS – Furniture and equipment purchased and installed by the PUBLIC ENTITY.

## 2. Creation of buildings. Needs
Supplement 2.1 document 3 "Technical requirements for the creation of headquarters"
| Project name |  | Development of a military campus infrastructure in Klaipėda district, Kairiai
| Facility |  | Kairiai military town
| Type of construction |  | New construction
| Annex to terms & conditions |  | Annex 2 Specifications
| Supplement |  | Supplement 2.1 document 3 "Technical requirements for the creation of headquarters"
| Supplement document (worksheet) |  | worksheet 2. Development of buildings. Needs
Item No. | The name of the room/space/functional block | Number of places | Phones connected to the KATT | Computer networks are connected to the unit's network 2 | Computer networks are connected to the KAS network 1 | Number of computerised workstations | Approximate area (sq. m) (if needed to determine) | The significance level of the room/space/functional block (A, B, C and D) | Description of special requirements for premises/areas (if applicable) | The area of the premises/space/functional block in square metres proposed by the Candidate/Participant | numbering of premises according to the explanations on the drawings proposed by the Candidate/Participant | Cost of development of the solution proposed by the Candidate / Participant (EUR excl. VAT) | Furniture/equipment inventory |  |  |  | Possible optimisation proposed by the Candidate – additional solutions to those in the Specification (reference to the Tender document, section, paragraph, clause). Price (EUR excl. VAT) This section is to be completed only for the Initial Tender | REMARKS
[13 empty] | Description of the building's furniture/equipment inventory needs and Special Requirements (if any) | The planned furniture/equipment inventory is purchased by *PS, **PS, or VS | The price of furniture and equipment proposed by the Candidate/Participant for the investor (which is purchased by the Private Entity) (*PS, **PS)) (EUR excl. VAT) | Cost for the installation of the furniture and equipment inventory proposed by the Candidate/Participant (*PS, **PS) (EUR excl. VAT)
| To be completed by the Public entity (PE). When submitting the Tender, the information “To be completed by the Candidate/Participant" may be suspplemented by the Candidate/Participant | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | to be completed by Candidate / Participant | to be completed by Candidate / Participant | to be completed by Candidate / Participant | To be completed by Public entity | To be completed by Public entity | to be completed by Candidate / Participant | to be completed by Candidate / Participant | To be completed by the candidate (only applicable for Initial Tender)
Headquarters (Type II)
1. | Administrative area | 179 | 112 | 13 | 123 | 119 | 1208
1.1. | Office | 1 | 1 | - | 1 | 1 | 30 | B | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide an office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | PS*
1.2. | Meeting room | 15 | 1 | - | 2 | 2 | 30 | B | The walls and ceilings must be built of brick, blocks, or constructed from metal sheets, solid wood, or similar materials providing equivalent resistance to break-ins. A designated space for a safe must be provided (400x300x300 mm). The door leaf and frame must be made of metal sheets less than 2 mm thick, solid wood, particleboard, plywood, glass, or similar materials ensuring equivalent resistance to burglary; the door must be fitted with a single lock with a cylindrical core or a lever lock. Window frames must be made of durable material, and the glass must be coated with a protective film. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide a meeting room set No. 6 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | PS*
1.3. | Office | 1 | 1 | - | 1 | 1 | 18 | B | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide an office furniture set No. 1 (according to document 29 of Supplement 2 of Annex 2.1 of the Terms) | PS*
1.4. | Meeting room | 12 | 1 | - | 2 | 2 | 24 | B | The walls and ceilings must be built of brick, blocks, or constructed from metal sheets, solid wood, or similar materials providing equivalent resistance to break-ins. A location for a safe must be assessed. (400x300x300 mm). The door leaf and frame must be made of metal sheets less than 2 mm thick, solid wood, particleboard, plywood, glass, or similar materials ensuring equivalent resistance to burglary; the door must be fitted with a single lock with a cylindrical core or a lever lock. Window frames must be made of durable material, and the glass must be coated with a protective film. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide a meeting room set No. 6 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | PS*
1.5. | Office | 1 | 1 | - | 1 | 1 | 18 | B | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide an office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | PS*
1.6. | Office | 1 | 1 | - | 1 | 1 | 18 | B |  |  |  |  | Provide an office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | PS*
1.7. | Office | 4 | 4 | 4 | 4 | 4 | 32 | B | The rooms are arranged according to the resolution of the Government of the Republic of Lithuania dated 2018-08-13 No. 820 requirements. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 4 room. |  |  |  | Provide for office furniture sets No. 2 and No. 3 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | PS*
1.8. | Office | 1 | 1 | - | 1 | 1 | 12 | B | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide an office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | PS*
1.9. | Office | 4 | 4 | - | 4 | 4 | 32 | B |  |  |  |  | Provide for office furniture sets No. 2 and No. 3 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | PS*
1.10. | Office | 2 | 2 | - | 2 | 2 | 16 | B |  |  |  |  | Provide for office furniture sets No. 2 and No. 3 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | PS*
1.11. | Office | 1 | 1 | - | 1 | 1 | 12 | A |  |  |  |  | Provide an office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | PS*
1.12. | Office | 1 | 1 | - | 1 | 1 | 12 | A |  |  |  |  | Provide for office furniture sets No. 2 and No. 3 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | PS*
1.13. | Office | 6 | 6 | 6 | 6 | 6 | 42 | A | The rooms are arranged according to the resolution of the Government of the Republic of Lithuania dated 2018-08-13 No. 820 requirements. which room requirements? Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 4 room. I or II security zone??? |  |  |  | Provide for office furniture sets No. 2 and No. 3 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | PS*
1.14. | Office | 1 | 1 | - | 1 | 1 | 12 | B | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide an office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | PS*
1.15. | Office | 5 | 5 | - | 5 | 5 | 36 | B |  |  |  |  | Provide for office furniture sets No. 2 and No. 3 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | PS*
1.16. | Office | 2 | 2 | - | 2 | 2 | 16 | B |  |  |  |  | Provide for office furniture sets No. 2 and No. 3 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | PS*
1.17. | Office | 1 | 1 | - | 1 | 1 | 12 | B |  |  |  |  | Provide an office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | PS*
1.18. | Office | 5 | 5 | - | 5 | 5 | 40 | B |  |  |  |  | Provide for office furniture sets No. 2 and No. 3 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | PS*
1.19. | Office | 5 | 5 | - | 5 | 5 | 40 | B |  |  |  |  | Provide for office furniture sets No. 2 and No. 3 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | PS*
1.20. | Office | 1 | 1 | - | 1 | 1 | 12 | B |  |  |  |  | Provide an office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | PS*
1.21. | Office | 3 | 3 | 3 | 3 | 3 | 18 | B | The rooms are arranged according to the resolution of the Government of the Republic of Lithuania dated 2018-08-13 No. 820 requirements. which room requirements? Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 4 room |  |  |  | Provide for office furniture sets No. 2 and No. 3 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | PS*
1.22. | Office | 2 | 2 | - | 2 | 2 | 16 | B | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide for office furniture sets No. 2 and No. 3 (according to document 29 of Supplement 2 of Annex 2.1 of the Terms) | PS*
1.23. | Office | 1 | 1 | - | 1 | 1 | 16 | B |  |  |  |  | Provide an office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | PS*
1.24. | Office | 1 | 1 | - | 1 | 1 | 16 | B |  |  |  |  | Provide an office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | PS*
1.25. | Office | 3 | 3 | - | 3 | 3 | 24 | B |  |  |  |  | Provide for office furniture sets No. 2 and No. 3 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | PS*
1.26. | Office | 3 | 3 | - | 3 | 3 | 24 | B |  |  |  |  | Provide for office furniture sets No. 2 and No. 3 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | PS*
1.27. | Office | 3 | 3 | - | 3 | 3 | 24 | B |  |  |  |  | Provide for office furniture sets No. 2 and No. 3 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | PS*
1.28. | Office | 3 | 3 | - | 3 | 3 | 24 | B |  |  |  |  | Provide for office furniture sets No. 2 and No. 3 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | PS*
1.29. | Office | 3 | 3 | - | 3 | 3 | 24 | B |  |  |  |  | Provide for office furniture sets No. 2 and No. 3 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | PS*
1.30. | Printing room (for maps) | 1 | 1 | - | 1 | 1 | 8 | C | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned.
1.31. | Office | 3 | 3 | - | 3 | 3 | 24 | B | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide for office furniture sets No. 2 and No. 3 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | PS*
1.32. | Office | 2 | 2 | - | 2 | 2 | 16 | B |  |  |  |  | Provide for office furniture sets No. 2 and No. 3 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | PS*
1.33. | Office | 2 | 2 | - | 2 | 2 | 16 | B |  |  |  |  | Provide for office furniture sets No. 2 and No. 3 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | PS*
1.34. | Office | 1 | 1 | - | 1 | 1 | 12 | B |  |  |  |  | Provide for office furniture sets No. 2 and No. 3 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | PS*
1.35. | Meeting room | 30 | 2 | - | 10 | 6 | 60 | A | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide a meeting room set No. 6 (according to document 28 of Annex 2 Supplement 2 of the Terms) | PS*
1.36. | Storage room | - | - | - | - | - | 20 | C | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 1 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide racks (according to document 26 of Annex 2 Supplement 2.1 of the Terms). | PS*
1.37. | Storage room | - | - | - | - | - | 20 | C |  |  |  |  | Provide racks (according to document 26 of Annex 2 Supplement 2.1 of the Terms). | PS*
1.38. | Storage room | - | - | - | - | - | 20 | C |  |  |  |  | Provide racks (according to document 26 of Annex 2 Supplement 2.1 of the Terms). | PS*
1.39. | Storage room | - | - | - | - | - | 20 | C |  |  |  |  | Provide racks (according to document 26 of Annex 2 Supplement 2.1 of the Terms). | PS*
1.40. | Storage room | - | - | - | - | - | 20 | C |  |  |  |  | Provide racks (according to document 26 of Annex 2 Supplement 2.1 of the Terms). | PS*
1.41. | Office | 1 | 1 | - | 1 | 1 | 18 | B | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 1 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned.
1.42. | Meeting room | 15 | 1 | - | 2 | 2 | 30 | B | The walls and ceilings must be built of brick, blocks, or constructed from metal sheets, solid wood, or similar materials providing equivalent resistance to break-ins. A designated space for a safe must be provided (400x300x300 mm). The door leaf and frame must be made of metal sheets less than 2 mm thick, solid wood, particleboard, plywood, glass, or similar materials ensuring equivalent resistance to burglary; the door must be fitted with a single lock with a cylindrical core or a lever lock. Window frames must be made of durable material, and the glass must be coated with a protective film. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned.
1.43. | Office | 1 | 1 | - | 1 | 1 | 18 | B | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide an office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | *PS
1.44. | Office | 3 | 3 | - | 3 | 3 | 24 | B | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide an office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | *PS
1.45. | Office | 2 | 2 | - | 2 | 2 | 16 | B | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide an office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | *PS
1.46. | Office | 2 | 2 | - | 2 | 2 | 16 | B | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide an office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | *PS
1.47. | Office | 1 | 1 | - | 1 | 1 | 12 | B | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide an office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | *PS
1.48. | Office | 1 | 1 | - | 1 | 1 | 12 | B | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide an office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | *PS
1.49. | Office | 3 | 3 | - | 3 | 3 | 24 | B | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide an office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | *PS
1.50. | Office | 2 | 2 | - | 2 | 2 | 16 | B | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide an office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | *PS
1.51. | Office | 1 | 1 | - | 1 | 1 | 12 | B | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide an office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | *PS
1.52. | Office | 3 | 3 | - | 3 | 3 | 24 | B | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide an office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | *PS
1.53. | Office | 2 | 2 | - | 2 | 2 | 16 | B | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide an office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | *PS
1.54. | Office | 2 | 2 | - | 2 | 2 | 16 | B | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide an office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | *PS
1.55. | Office | 2 | 2 | - | 2 | 2 | 16 | B | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide an office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | *PS
1.56. | Office | 2 | 2 | - | 2 | 2 | 16 | B | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide an office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | *PS
1.57. | Office | 5 | 5 | - | 5 | 5 | 36 | B | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide an office furniture set No. 1 (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | *PS
2. | Special-purpose room zone: | 278 | 9 | 30 | 9 | 32 | 648
2.1. | Document storage room | - | - | - | - | - | 8 | B | The rooms are arranged according to the resolution of the Government of the Republic of Lithuania dated 2018-08-13 No. 820 requirements. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 5 room. |  |  |  | Provide all required equipment and furniture required for the room's functionality. | *PS
2.2. | Document storage room | - | - | - | - | - | 8 | B | The rooms are arranged according to the resolution of the Government of the Republic of Lithuania dated 2018-08-13 No. 820 requirements. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 5 room. |  |  |  | Provide all required equipment and furniture required for the room's functionality. | *PS
2.3. | Document processing room. | 10 | 1 | 10 | - | 10 | 60 | B | The rooms are arranged according to the resolution of the Government of the Republic of Lithuania dated 2018-08-13 No. 820 requirements. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 4 room. |  |  |  | Provide an office furniture set No. 2 (4 units). | *PS
2.4. | Meeting hall | 30 | 1 | 5 | - | 2 | 60 | B | The rooms are arranged according to the resolution of the Government of the Republic of Lithuania dated 2018-08-13 No. 820 requirements. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 4 room. |  |  |  | Provide a meeting room set No. 6 (according to document 28 of Annex 2 Supplement 2 of the Terms) | *PS
2.5. | Meeting hall | 30 | 1 | 5 | - | 2 | 60 | B | The rooms are arranged according to the resolution of the Government of the Republic of Lithuania dated 2018-08-13 No. 820 requirements. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 4 room. |  |  |  | Provide a meeting room set No. 6 (according to document 28 of Annex 2 Supplement 2 of the Terms) | *PS
2.6. | Server room | - | - | - | - | - | 8 | B | The rooms are arranged according to the resolution of the Government of the Republic of Lithuania dated 2018-08-13 No. 820 requirements. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 5 room.
2.7. | Storage room | - | - | - | - | - | 18 | C | The rooms are arranged according to the resolution of the Government of the Republic of Lithuania dated 2018-08-13 No. 820 requirements. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 5 room. |  |  |  | Provide racks (according to document 26 of Annex 2 Supplement 2.1 of the Terms). | *PS
2.8. | Class | 10 | 1 | 10 | 1 | 10 | 60 | B | The rooms are arranged according to the resolution of the Government of the Republic of Lithuania dated 2018-08-13 No. 820 requirements. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 4 room. |  |  |  | Provide a meeting room set No. 6 (according to document 28 of Annex 2 Supplement 2 of the Terms) | *PS
2.9. | Recreation room | 1 | - | - | - | - | 30 | C | The room must include a utility space (a sink with hot and cold water connections, disposable towel and detergent dispensers, kitchen cabinets – 2 units, additional installation of 4 electrical outlets, space for a refrigerator). The refrigerator is purchased by the VS. Magnetic contacts for protective alarms are to be installed on the window sashes and assigned to the high corridor area. |  |  |  | Provide a set of rest furniture No. 5 (according to document 28 of Annex 2 Supplement 2.1 of the Terms. | *PS
2.10. | Recreation room | 1 | - | - | - | - | 30 | C | The room must include a utility space (a sink with hot and cold water connections, disposable towel and detergent dispensers, kitchen cabinets – 2 units, additional installation of 4 electrical outlets, space for a refrigerator). The refrigerator is purchased by the VS. Magnetic contacts for protective alarms are to be installed on the window sashes and assigned to the high corridor area. |  |  |  | Provide a set of rest furniture No. 5 (according to document 25 of Annex 2 Supplement 2.1 of the Terms. | *PS
2.11. | Sanitary unit rooms with showers, toilets, and washbasins | 65 | - | - | - | - | 50 | C | Magnetic contacts for protective alarms are to be installed on the window sashes and assigned to the high corridor area. |  |  |  | Provide all required equipment and furniture required for the room's functionality. | PS
2.12. | Sanitary unit rooms with showers, toilets, and washbasins | 25 | - | - | - | - | 30 | C | Magnetic contacts for protective alarms are to be installed on the window sashes and assigned to the high corridor area. |  |  |  | Provide all required equipment and furniture required for the room's functionality. | PS
2.13. | On-duty room | 2 | 1 | - | 2 | 2 | 24 | A | The room must be designed as the main (central) monitoring and control space of the military unit, where personnel on duty can monitor the status of all military unit security, fire protection, and other systems and manage key functions. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Remote workstations for the EAS system |  |  |  | Provide space for office furniture set No. 2 (2 units). | *PS
2.14. | Weapons storage room | 60 | - | - | 1 | 1 | 30 | A | The premises must be set up following the order of the Minister of National Defence of the Republic of Lithuania dated 26 March 2009. No. V -254 (or other relevant current versions of the legal acts in force during the formation or execution of the Contract, or the versions of orders replacing these orders). The layout of the weapons storage room is recommended to follow the Barracks Planning Norms, approved by the Minister of National Defence on 1 August 2000, Order No. 875. The room must be designed and equipped with 5 units of weapon racks (according to document 1 of Annex 2 Supplement 2 of the Terms). Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 3 room. Access control system – not planned. |  |  |  | The room must include space for 2 safes intended for storing ammunition (according to document 25 of Annex 2 Supplement 2 of the Terms). Access to the armoury room is only possible through doors equipped with personal identification measures (a card-based movement control system is planned, integrated with and forming part of the overall building access control system). | *PS
2.15. | Weapons storage room | 40 | - | - | 1 | 1 | 20 | A | The premises must be set up following the order of the Minister of National Defence of the Republic of Lithuania dated 26 March 2009. No. V -254 (or other relevant current versions of the legal acts in force during the formation or execution of the Contract, or the versions of orders replacing these orders). The layout of the weapons storage room is recommended to follow the Barracks Planning Norms, approved by the Minister of National Defence on 1 August 2000, Order No. 875. The room must be designed and equipped with 5 units of weapon racks (according to document 1 of Annex 2 Supplement 2 of the Terms). Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 3 room. Access control system – not planned. |  |  |  | The room must include space for 2 safes intended for storing ammunition (according to document 25 of Annex 2 Supplement 2 of the Terms). Access to the armoury room is only possible through doors equipped with personal identification measures (a card-based movement control system is planned, integrated with and forming part of the overall building access control system). | *PS
2.16. | Archive room | 1 | 1 | - | 1 | 1 | 40 | A | To optimise the use of allocated space, cabinets must be designed and installed according to the order of the Chief Archivist of Lithuania, dated 28 December 2011, No. V -157 “On the Approval of Document Storage Rules.” Mobile archival shelving, lockable metal safes/cabinets must be installed for document storage. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide all required equipment and furniture required for the room's functionality. | *PS
2.17. | Archive room | 1 | 1 | - | 1 | 1 | 40 | A | To optimise the use of allocated space, cabinets must be designed and installed according to the order of the Chief Archivist of Lithuania, dated 28 December 2011, No. V -157 “On the Approval of Document Storage Rules.” Mobile archival shelving, lockable metal safes/cabinets must be installed for document storage. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 2 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned. |  |  |  | Provide all required equipment and furniture required for the room's functionality. | *PS
2.18. | Server room 1/2 | - | - | - | - | - | 16 | A | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 4 room.
2.19. | Electronic security systems communication room – server room | - | - | - | - | 0 | 10 | A
2.20. | Telecommunications equipment room | - | - | - | - | 0 | 12 | A
2.21. | Communication entry room (hardware) | - | - | - | - | 0 | 6 | A
2.22. | Administrator's room | 1 | 1 | - | 1 | 1 | 16 | A | Access to the server room must be planned through this room. The walls and ceilings must be built of brick, blocks, or constructed from metal sheets, solid wood, or similar materials providing equivalent resistance to break-ins. A location for a safe must be assessed. (400x300x300 mm).Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 4 room. |  |  |  | Provide space for office furniture set No. 2 (2 units). | *PS
2.23. | Administrator's room | 1 | 1 | - | 1 | 1 | 12 | A | Access to the server room must be planned through this room. The walls and ceilings must be built of brick, blocks, or constructed from metal sheets, solid wood, or similar materials providing equivalent resistance to break-ins. A location for a safe must be assessed. (400x300x300 mm).Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 4 room. |  |  |  | Provide space for office furniture set No. 2 (2 units). | *PS
3. | Technical rooms | 0 | 0 | 0 | 0 | 0 | 46
3.1. | Technical rooms | - | - | - | - | - | 26 | A | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 1 room, Video surveillance – general monitoring of building access points and entrances, Access control system – not planned.
3.2. | Electronic security systems switch room | - | - | - | - | - | 6 | A | A separate EAS communication room must be installed on every second floor of the building. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 4 room.
3.3. | Switching room (communication distribution point) | - | - | - | - | - | 14 | A | A separate communication room must be installed on each floor of the building if computer workstations are planned (the communication room area must be no less than 6 m²) Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 4 room.
4. | Other rooms: | [5 empty] | 336
4.1. | Corridor | - | - | - | - | - | 330 | C | At the main entrance to the building (inside the building), solutions for washing soldiers' feet (shoes) upon returning from activities must be provided. At each entrance to the building, 15 foot (shoe) washing tubs must be provided. The foot washing area must have a water supply, a solution for washing feet (shoes), and a solution for collecting and removing the residual water during and after washing. Corridors must have designated space for the drinking water inlet and space for the installation of electrical networks for a coffee/snack machine. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 1 room, Video surveillance – general monitoring of access to the building and building entrances inside the corridor, Access control system – Access must be provided at all exterior entrance doors to the building, allowing personnel direct access to the security office control window (further access to the corridor is controlled by access control).An intelligent key issuance cabinet must be installed next to the security office (300 key slots and 10 compartments for key bundles). A certified stationary breathalyser with facial recognition must be installed next to the security office. |  |  |  | In the corridors, designate a location with an electrical outlet for placing a coffee/snack machine; in the corridors, designate a location for a drinking water dispenser | *PS
4.2. | Cleaning inventory storage room (on each floor) | - | - | - | - | - | 6 | C | Each floor of the building must include technical rooms for storing cleaning equipment. Forced air extraction must be ensured in these rooms, with a sink equipped with hot and cold water connections, and holders must be provided for convenient storage of brushes and other tools. |  |  |  | Provide all required equipment and furniture required for the room's functionality. | *PS
5. | Other. Proposed by the Candidate / Participant. | [16 empty] | The Candidate / Participant may add to the Solution / Tender its own solutions that are not in conflict with the Specification or not evaluated by the Public Entity (PE)
| Total building area | [5 empty] | 2238
The price must match the price of part of the Facility of Supplement 2.1, document 1, worksheet 1
[12 empty] | Total (EUR, excl. VAT) |  |  |  |  | Total cost of the optimisation solutions (EUR excl. VAT). Cost of additional work or savings
REMARKS:
1. The Public Entity fills in the specifications, object data, and design task taking into account the features and purpose of the object.
2. The Public Entity provides known special requirements and descriptions of objects, rooms, spaces, functional blocks, and infrastructure. If descriptions are not provided in the Public Entity tables, the Candidate/Participant must submit their tenders in accordance with applicable regulations, standards, and other legal acts.
3. The Candidate/Participant may propose and suggest possible optimisations in their solutions (by suggesting to supplement the Specifications, justifying the benefits of the proposals and their impact on the price of the Tender).
4. The Public Entity classifies rooms/ spaces/ functional blocks by significance levels into functional sector significance levels A, B, C, and D (Specifications section "Functional sectors").
5. The areas provided in the table are approximate and may change depending on the implementation of regulatory acts and the requirements of the Specifications.
6. The technological rooms must be equipped with an air conditioning system, ensuring the proper operating conditions for the equipment installed in these rooms. Parameters are selected according to the recommendations of computer network equipment manufacturers. Temperature deviations in the rooms must be automatically recorded in the Registration Tool.
7. The size of technological premises indicated in the table is approximate, it is adjusted by evaluating the planned equipment quantities to be installed. The size of the room must allow easy access to the switchgear cabinets and equipment maintenance.
10. Technological rooms should not be located beneath sanitary facilities or in other areas where there is a high risk of flooding.
11. If necessary to clarify the solutions, the Participant may add rows to their table.
12. * The PS must provide for a one-time furniture purchase and warranty maintenance for a period of 5 years
13 **The PS must provide equipment/furniture that is mandatory (or necessary) for the proper functioning (use) of buildings/premises, in accordance with legal acts/regulations, the Private Entity’s solutions, etc., including their further technical maintenance throughout the entire Contract period
14. VS – Furniture and equipment purchased and installed by the PUBLIC ENTITY.

## 3. Development of buildings. Co
Supplement 2.1 document 3 "Technical requirements for the creation of headquarters"
| Project name | Development of a military campus infrastructure in Klaipėda district, Kairiai
| Facility | Kairiai military town
| Type of construction | New construction
| Annex to terms & conditions | Annex 2 Specifications
| Supplement | Supplement 2.1 document 3 "Technical requirements for the creation of headquarters"
| Supplement document (worksheet) | worksheet 3. Development of buildings. Construction
Item No. | Building part/ System/ Area | Description of special requirements for premises/areas (if applicable) | Headquarters No. 1
|  |  | Description of solutions proposed by the Candidate/Participant (reference to the annex of the Tender: Section, part, item of the Tender). | Cost of development of the solution proposed by the Candidate / Participant (EUR excl. VAT) | Possible optimisation proposed by the Candidate – additional solutions to those in the Specification (reference to the Tender document, section, paragraph, clause). Price (EUR excl. VAT) This section is to be completed only for the Initial Tender | REMARKS
| To be completed by the Public entity (PE). When submitting the Tender, the information “To be completed by the Candidate/Participant" may be suspplemented by the Candidate/Participant | to be filled by the Public Entity (if specific requirements are known and applied | to be completed by Candidate / Participant | to be completed by Candidate / Participant | To be completed by the candidate (only applicable for Initial Tender)
1. | Building structures and other elements
1.1. | Foundations | Foundations under supporting structures must be designed considering the loads, the nature of the load increase, and the foundation ground properties. The final decision on the type of foundation must be based on the results of engineering geological studies and a cost comparison of different foundation types. The Participant provides information on selected foundation type, including structures, insulation, and finishing materials etc.
1.2. | Plinth installation | Wall covers (by the type of coating) must be compatible with the room purpose, resistant to wet cleaning and, where necessary, to chemicals used for disinfection. The Participant provides information on plinth solutions, finishing materials etc.
1.3. | Load-bearing external walls, structures | 1. For rooms subject to stricter security requirements, the exterior walls must ensure increased security (e.g., for weapons, document storage, and other rooms). 2. The areas designated for soldier movement must be separated from the external building enclosures to protect the building façades and their external elements from accidental damage. If necessary, external wall cladding must be used, ensuring its acoustic properties. Colours and materials must be selected based on resistance to dirt, ease of cleaning, material aging, wear, and simplicity of maintenance. 3. The architecture of the building's facade must be simple (without intricate details). Facades must be easy to maintain and durable, with facade materials offering increased resistance to dirt and damage. Facade materials must be resistant to adverse climatic effects and urban pollution and/or biological materials (moss, mould, insects, rodents, bird droppings) et al). 4. When the perimeter fence of the military unit coincides with the building wall, the elements of this wall, which are up to 2.5 metres in height, must meet the requirements for a minimum of 2 burglary resistance ratings. If there are trees, buildings, or other objects near the fence that can be used to climb over it, the fence's resistance to intrusion score must be lowered by two points. 5. Wall covers (by the type of coating) must be compatible with the room purpose, resistant to wet cleaning and, where necessary, to chemicals used for disinfection. The Participant provides information on external wall solutions, including structures, insulation, and finishing layers etc.
1.4. | Non-load-bearing external walls, structures
1.5. | Slabs on the ground. | 1. Acoustic noise in shared areas must not exceed 85 dBA, in work offices and meeting rooms – up to 50 dBA, and in sleeping areas – up to 32 dBA. 2. In special rooms with a high or medium potential for liquid accumulation, a floor slope must be installed to allow liquids to drain into the sewage system. 3. Floor coverings must be suitable for their intended use based on the function of the rooms or spaces where they are installed. 4. The floors must be designed to withstand their own weight and operational loads, considering the intended purpose of the rooms. The participant provides information about the floor slab structure (insulation types, layers) etc.)
1.6. | Floor slabs between levels
1.7. | Roof | 1. Measures to prevent the formation of icicles must be provided; 2. The roof must be easy to maintain, with maintenance walkways and platforms installed. Access to the roof must be easy but restricted with safety measures to prevent unauthorized individuals from accessing it; 3. Water from the building’s roof must be drained in such a way that it does not damage the building’s structure, roads, sidewalks, adjacent buildings, or harm the environment, and is directed into the underground stormwater drainage system. The participant provides information about the roof structure, insulation types and layers, and finishes. Rainwater collection and drainage system, roof protective railings, walkways, protective grilles, snow-retaining grilles, fire escape ladders etc.
1.8. | Load-bearing internal walls | Wall covers (by the type of coating) must be compatible with the room purpose, resistant to wet cleaning and, where necessary, to chemicals used for disinfection. The Participant provides information on internal wall solutions, including structures, insulation, and finishing layers etc.
1.9. | Non-load-bearing internal walls | Wall covers (by the type of coating) must be compatible with the room purpose, resistant to wet cleaning and, where necessary, to chemicals used for disinfection. The Participant provides information on internal wall solutions, including structures, insulation, and finishing layers etc.
1.10. | Structural elements | The structure of the buildings must be durable enough to withstand the negative effects of rare and potentially dangerous events. The main criterion when choosing building materials is public safety and material durability. These materials must be used in such a way that they meet the requirements or are of better quality than those specified in the technical requirements of these Specifications. The Participant provides information on stairs, ramps, balconies, and loggia structures, including coatings etc.
1.11. | Partitions | The finishing of partitions can be minimal (for example, where allowed by the construction norms, walls can be left unplastered, painted, or impregnated), but must comply with the intended use of the rooms. Wall covers (by the type of coating) must be compatible with the room purpose, resistant to wet cleaning and, where necessary, to chemicals used for disinfection. Work offices in the administrative area (No. 1.11., 1,13.) The walls and ceilings/floors must be made of perforated ceramic brick masonry of at least 200 mm thick, or metal sheets of at least 3 mm thick, or solid wood at least 120 mm thick, or perforated brick or block masonry of at least 250 mm thick, or solid silicate brick masonry of at least 120 mm thick or similar materials providing equivalent resistance to break-ins. The Participant provides information on Partition types, structures, finishes etc.
1.12. | Floor coverings and finishes. | The floors in sanitary rooms/ spaces/ areas must be non-slip, waterproof, easy to clean, resistant to the cleaning agents and disinfectants used, and must have a slope towards the water drainage channels for self-collection into the sewage system. Floor and stair surfaces must be non-slip, easy to clean, and resistant to the chemicals used for wet cleaning and disinfection. The Participant provides information on floor type, structures, finish. The main room groups are distinguished – corridors, halls, administrative rooms, service rooms, and technical auxiliary rooms etc.
1.13. | Wall finish | 1. Design the facades of buildings, considering the purpose of the buildings, the cohesive architectural appearance of the area, and long-term durability. 2. The interior wall finishes can be minimal (for example, where construction regulations allow, walls can be unplastered and painted or impregnated), but they must meet the room's intended use. Walls in building rooms may be impregnated with clear liquids or impregnating paints. 3. The wall covering (according to the type of covering) must match the room’s purpose, be resistant to damp cleaning, and where necessary, resistant to chemicals used for disinfecting. Where walls are to be painted, they must be painted with eco-friendly paints. Walls may also be coated with other high-quality and suitable coverings matching the purpose of the room. 4. In sanitary units, the walls must be covered with ceramic tiles, and the cabin walls must be elevated from the floor and made of chipboard (MDP) or laminated panels (HPL), both with an aluminium frame. The participant provides descriptions of wall construction types, frame infills, and finishes etc.
1.14. | Ceiling finishing | The ceiling finishing may be minimal, but it must comply with the intended use of the room. The Participant provides information on ceiling types, structures, finishes etc.
1.15. | External doors, windows, and showcases | Outdoors must be equipped with direct-acting electromagnetic valves. Where required by special regulations, protective metal grills should be installed, and access to windows from the exterior of the building should be restricted. The Participant provides information on windows, showcases, doors, gates, including sills, trims, fittings, drive mechanisms, micro-ventilation elements, and other installed components.
1.16. | Skylights | The Participant provides information on skylights, roof hatches, including trims, fittings, drive mechanisms, ventilation elements, and other installed components.
1.17. | Internal doors and windows | 1. Internal doors, depending on the purpose, security, and number of operating cycles – metal, plastic, aluminium, or wooden (veneered). Fittings must be adapted to the designated use of the premises. Entrance doors to security zones (electronic security system requirement rooms of types 4 and 5) must be equipped with direct-acting electromagnetic locks (without a free passage function), scanning devices, and, if required, intercom systems. Doors must be designed to provide sound insulation where required, withstand increased operational loads, and be easy to operate. Access control door exit from the indoors must also be provided with a handle; these doors must also be lockable with a mechanical lock. Access to designated zones (detailed in Supplement 2.1 "Building, Structure, and Territory Specifications") must be restricted. In high-traffic areas, doors must also be protected with galvanised steel plates covering up to half their height. In areas where specific architectural solutions are required for internal equipment, other protective measures may be proposed. Access to doors and movement zones must be protected from damage and accelerated material wear. Information plates must be installed on doors. Information plates must be installed on interior doors and at entrances to each floor’s rooms, allowing for easy modification of displayed information. The information to be specified on the arrows and information boards will be determined by the Public Entity. All internal doors must have locks controlled by keys. There must be a manual method to open the electric skis using a key in case they do not work. The Participant provides information on interior room windows, showcases, doors, gates, including sills, trims, fittings, drive mechanisms, and other installed components. Work offices in the administrative area (No. 1.11., 1,13.) Doors must be equipped with at least two locks, one with a cylindrical core tested in accordance with standard 1303, meeting at least security class 4 requirements, and the other being a lever lock. Testing of both lock bodies must be carried out in accordance with standard 12209 and must meet at least Level 4 requirements. If the door contains glass, it must be tested according to standard 356 and meet resistance requirements of at least P5A or be covered with a protective film no thinner than 400 microns, and: 1) testing of door leaves and frames must be carried out in accordance with standard 1627 and must meet security requirements of at least RC classification or higher. 2) The door leaf must be made of profile steel. The pipe profile must be no thinner than 20 x 28 mm, with a wall thickness no thinner than 1.5 mm, and must be installed along the entire perimeter of the frame. The installation location of the lock is reinforced with a box made of pipe profile of at least 20 x 28 mm thick along the entire perimeter of the lock in the plane of the door. If the width of the leaf exceeds 800 mm, an additional support must be installed across the full height of the leaf. The gap between the door leaf and the frame must not exceed 6 mm. Stone wool infill no thinner than 28 mm. On the outer leaf side, a steel sheet, at least 1.5 mm thick, is placed on the tubular profiles. The sheet, no less than 12 mm, must cover the gap between the frame and the door leaf. A steel sheet, at least 1.5 mm thick, is attached to the inner side of the leaf frame. The frame is made of profile steel, with dimensions not smaller than 80 x 40 mm, and the wall thickness not less than 3 mm. The frame must be fixed at least at six points with metal rods or bolts with a diameter of no less than 14 mm, or masonry pins with a diameter of no less than 12 mm and a length of 150 mm. The gap between the frame and the wall, after inserting rods, must be filled with a cement mortar mixture. At least three metal pins with a diameter of no less than 12 mm and length of 15 mm must be installed on the hinge side. The Participant provides information on interior room windows, showcases, doors, gates, including sills, trims, fittings, drive mechanisms, and other installed components.
1.18. | Sun protection | External heat gain management must be planned by selecting equipment (devices) that limit direct sunlight from entering the rooms. They can be controlled mechanically when installed inside or be installed on the exterior of the window (room), in which case their control must be electric. The sun protection measures to be installed must be designed for increased operational load, as well as being easy and simple to maintain, with the ability to limit or even stop direct sunlight, while allowing diffuse light to pass through. The Participant provides information on roller blinds, awnings, and shutters, including drive mechanisms etc.
1.19. | Special built-in elements | Outdoor stair railings, handrails, joints, and covering elements must be installed from stainless steel pipes. Outdoor stair railings, handrails, joints, and covering elements must be made of stainless steel. The Participant provides information on grilles, railings, handrails, decorative and covering elements (light well covers, foot cleaning grates) et al).
1.20. | Other | Work offices in the administrative area (No. 1.11., 1,13.) Grilles must be made of 45 x 6 mm steel flat bars, with a maximum spacing of 200 mm between them. Steel rods with a diameter of no less than 20 mm must be embedded into the bars every 150 mm. Opening grille fastening rods must be embedded in the wall to a depth of at least 200 mm. Swinging grilles must be locked with locks in at least two places, whose cylindrical cores must be tested according to standard 1303 and meet at least the requirements of security class 6; padlocks must be tested according to standard 12320 and must meet at least security level 6 requirements.
1.21. | Other. Proposed by the Candidate / Participant. | The Candidate / Participant may add to the Solution / Tender its own solutions that are not in conflict with the Specification or not evaluated by the Public Entity (PE)
2. | Building internal engineering systems
2.1. | Heating systems and equipment | It is necessary to install heat consumption metering. Measuring devices must have a continuous scanning function. The possibility of adapting the heating installation for the functional separation of the military unit facility must be planned, taking into account the ability to normalise the temperature in different areas and rooms of the military unit facility by location and time, as well as the momentary increase or loss of heat, separately measuring heat consumption in separated facilities, and smoothly adjusting parameters to ensure continuous adaptation to demand, including at different times of the day. Areas where underfloor heating will be installed must be planned in such a way that they do not interfere with future furniture attachment. The participant provides a description – heat supply, heating system, heat production, heating pipelines etc. Radiators, underfloor heating, radiant heating systems etc. Metering.
2.2. | Ventilation systems and equipment | Air conditioning must be installed in work offices and server rooms. In the server rooms and uninterrupted power supply room, a separate automated precision control air conditioning system must be provided. Separate electrical panels must be provided for air conditioning equipment, and a separate grounding loop must be provided for the equipment. A constant temperature of 20–25 °C and relative humidity of 40–55% must be maintained in these rooms. The conditioning system is duplicated: one working and the other backup units. The backup air conditioner must activate automatically by rotating if the temperature in the room increases or in the event of the main air conditioner failure; In the server rooms and uninterrupted power supply room, a separate ventilation system must be provided; engineering systems not directly related to these rooms should not be installed there. Rooms must be protected from water flooding. The Participant provides information on air supply and extraction units, with or without air treatment functionality, ventilation equipment, technical air system ventilation systems, ducts and pipelines, ventilation openings and grilles, cooling systems, ducts and pipelines.
2.3. | Cooling (air conditioning) systems and equipment | The components of the cooling system must have an anti-condensation insulating layer; Water cooling system distributors (cartridges, air conditioning pipe equipment, brackets) in accessible locations must have regulating and shut-off valves to allow for system operation and control; The system must be connected to the general control system of the military unit; To cool the server rooms, precision-controlled air conditioners must be installed, which operate at low outdoor temperatures, as well as an air supply and exhaust system connected to the building’s control system. It is recommended to assess the possibility of creating the necessary engineering solutions to recover/reuse heat emitted in server rooms. The Participant provides information on selected cooling (air conditioning) system and equipment.
2.4. | Water supply and sewage systems and equipment | Anywhere sound may be heard from the wastewater piping, low-noise – thick-walled piping must be used, which must be additionally insulated; The accessibility of revisions installed on the sewage stands and the cleaning of the sewage disposal network must be planned to be free and convenient. The Participant provides information on water supply pipelines, sanitary fixtures, filters, drinking water supply, metering etc.
2.5. | Water metering installation | It is necessary to install water consumption measurement devices with a remote reading function; To ensure the required water consumption rates and the fire water supply system needs, appropriate equipment must be selected and installed Main water supply pipelines to all Military Unit Objects must have separate meters and distribution. The Participant provides information on water metering etc.
2.6. | Cold water system | The water supply in the military unit's objects must be designed so that water is supplied to all collection points, taking into account the pressure, flow rate, water properties, and the purpose of the building's use, as well as peak water consumption at the same time. When different requirements are set for the parameters of the water used at the collection points, water can be supplied through independent pipelines or water supply systems, providing water with the required properties from the corresponding external water supply networks or systems, which appropriately prepare the water. Water supply and distribution must be sufficient and meet the requirements of hygiene standards and other legal acts. Water consumption metering devices with remote reading functionality must be installed. Separate metering must be installed for each system with different water consumption purposes. Sanitary equipment must be aesthetic, durable, modern, and suitable for the functional area in which it is installed, and must comply with sanitary requirements. Water must be supplied to the facilities by connecting them to the main water supply network. The equipment must be installed to ensure that the water consumption indicators for the building complex are no less than the standard values and that the fire protection water supply needs are met. If the supplied water quality is insufficient, it must be achieved through appropriate water treatment engineering solutions. The number of drinking water supply points must be determined in accordance with regulations and standards. The Participant provides information on the proposed cold water supply system.
2.7. | Hot water systems and equipment | 1. The water supply system must ensure that water is supplied to all water usage points according to pressure, flow rate, and water characteristics requirements, peak water consumption at one time, and the designated purpose of the Military unit’s facilities. It is necessary to install water consumption measurement devices with a remote reading function; To ensure the required water consumption rates and the fire water supply system needs, appropriate equipment must be selected and installed The Participant provides information on water supply pipelines, sanitary fixtures, filters, hot water supply, metering etc.
2.8. | Domestic wastewater systems and equipment | Wastewater must be collected and directed according to economically/technically justified solutions, issued technical conditions. Toilet pots must have a water barrier inside. Water to toilet cisterns must be supplied silently (quiet operation), using no more than 6 l / 3 l of water for flushing. Urinals must have a contactless tap. In all buildings, except for the barracks washbasins near the WC (or closest to them), contactless taps with temperature limiters must be installed, as well as solutions for legionella prevention or pipe cleaning, preventing stagnant water from forming in the pipes (especially at the furthest points/water taps). In the barracks, one of the four mixers must be contactless. All sanitary devices, drain receivers, faucets, and other plumbing fixtures must be certified according to the ISO 9000 series or equivalent standard and meet the sizes specified by EN standards, with CE marking. Plumbing appliances installed in the facility must meet the following general requirements: their interior and exterior must have a smooth, easily cleanable surface (all appliances can be made of stainless steel); they must not have sharp protruding parts (in the appliance and in the fixing details); washbasins must be equipped with chrome-plated metal siphons that match the colour of the water mixing taps and faucets; toilet bowls must be equipped with seats and covers made of durable plastic. The participant provides a description – wastewater pipelines, wastewater collection facilities, wastewater treatment facilities Wastewater treatment plants
2.9. | Surface water drainage, rainwater systems, and devices | Rainwater drainage from the structures must be ensured, collected, and channelled according to the issued sewage network connection conditions. The participant provides a description – wastewater pipelines, wastewater collection facilities, wastewater treatment facilities etc.
2.10. | Plumbing appliances | Sanitary equipment must be aesthetic, durable, modern, and suitable for the functional area in which it is installed, and must comply with sanitary requirements. Sanitary infrastructure must be equipped with soap dispensers, hand dryers, paper towel dispensers, toilet paper dispensers, and automatically switched on and off lights. The Participant provides information on sanitary appliances, equipment, and systems
2.11. | Other equipment | The Participant provides information on other equipment not included in the listed water supply and wastewater disposal systems.
2.12. | Electrical systems and equipment | Locations and movement paths with few users or where users are not always present must be equipped with occupancy sensors. This is particularly important in storage and inventory areas, as well as in places with low movement. The quality of the equipment and the thoughtful placement of occupancy detectors must ensure complete convenience, as the lights must always turn on and off at the required times. Artificial lighting must be coordinated with surveillance equipment spaces and arranged so as not to dazzle the video surveillance cameras. The private partner must aim to reduce the number of lighting source models used. All equipment must be accessible for cleaning and maintenance, especially in high locations. Outdoor lighting must be controlled from the room. The lighting of auxiliary rooms must be distributed according to functional zones, but the lighting of zones related to event functions must be centralized and controlled from a dedicated room. A sufficient power capacity three-phase power supply must be planned (for all planned equipment). The electrical networks of the buildings must be designed for all types (facades, territories, fire extinguishing equipment, local television networks, fire hydrant light indicators, safety signs, call systems, light enclosures). and others) to power the lighting. Electrical cable installation must comply with the technical requirements for this system’s installation. In the building's premises, all installed control and protection devices must have a label indicating the schematic dependency and purpose. There must be a label with the name of the recipients and the line's purpose in the internal part of the door panel, on the panel by the devices. The Participant provides information on high and/or medium voltage distribution equipment. Electric power generators, including cooling, exhaust gas and fuel supply systems, central battery and uninterruptible power supply equipment, and photovoltaic systems. Cables, wires, secondary distributors, routing systems, installation devices. Fixed lights, including electric lamps. Lightning protection, lightning rod, and grounding systems. Electricity metering.
2.13. | Security alarm systems and devices | The general requirements of the system are described in Suplement 2.1 document 36 "Requirements for Electronic Protection Systems". The Participant provides information on protection alarm system and equipment.
2.14. | Access control systems and devices. | If card readers are installed outdoors, they must be mechanically sturdy and resistant to atmospheric conditions. In an emergency (power failure), control-operated doors must be unlockable with a key. The general requirements of the system are described in Suplement 2.1 document 36 "Requirements for Electronic Protection Systems". The Participant provides information on electromagnetic or mechanical locks. Access control system and devices.
2.15. | Video surveillance systems and equipment | The general requirements of the system are described in Suplement 2.1 document 36 "Requirements for Electronic Protection Systems". The Participant provides information on video surveillance cameras, video recording, storage, and display equipment.
2.16. | Computer and telephone networks | When designing telecommunications and computer networks and installing premises for primary equipment, the Cyber Defence Service of the Lithuanian Armed Forces (LK KGV ITT) must be provided with equipment room layouts, communication cables, networks, switching blocks, workstations, power and grounding system schemes in electronic format. When designing and constructing buildings and installing Equipment for Networks 1 and 2, representatives from the Cyber Defence Service of the Lithuanian Armed Forces (LK KGV ITT) must take part, in addition to other officials. The participant independently selects a communication provider required for PS needs and/or IP TV service provision. VS organizes the connection and service provision of the Ministry of Defence data transmission network. The Participant provides information on purpose of communication network, switch cabinet locations in the building, network switches, accessories, and other equipment.
2.17. | Automation systems and devices | A closed (local) building management system must be installed, allowing both monitoring and control of the main engineering system parameters. The accounting data analysis and processing software must be installed, designed for processing water, heat, electricity, and other meter data, generating reports, data analysis, and forecasting future needs. With the help of the installed systems, it must be possible to monitor and record the main microclimate parameters of at least five typical rooms (spaces). Meter readings must be transmitted automatically. The storage of copies of the transmitted telemetry data must be ensured. The Participant provides information on automated systems, control and monitoring devices, programming devices, sensors and actuators, communication intersection stations, and software for automated stations.
2.18. | Smoke extraction systems and equipment | The smoke extraction system and/or solution must be installed in accordance with the applicable regulations and standards. The Participant provides information on smoke extraction system, ducts, and equipment.
2.19. | Fire systems, fire detection systems, and equipment | The Participant provides information on fire detection and fire alarm systems.
2.20. | Fire extinguishing systems and equipment | The fire water supply system must comply with the applicable standards. The private partner must design an adequate number of external fire-fighting measures, considering the changes in the water supply system and fire safety standards. The private partner, considering the number of users in a specific Military Unit Object, must ensure appropriate evacuation conditions, ensuring that users can quickly and safely leave the danger zone or the area where a fire has occurred. Also, the appropriate structure, dimensions, and other technical fire safety measures must be ensured. The Participant provides information on fire suppression systems and devices.
2.21. | Gas pipeline system and equipment | The Participant provides information on gas pipeline networks, boilers, system and other equipment, metering.
2.22. | Specific use devices, other technological devices and systems | The Participant provides information on built-in elements for special purposes, signposts, informational and directional signs, colour-coded guidance systems, air compressors, liquid storage tanks etc.
2.23. | Renewable energy systems and devices are installed in the building. The system and equipment installed in the area are not evaluated here; such information is provided in the "Territory" worksheet before the field of engineering networks and systems. | The participant provides descriptions of systems and equipment, technical parameters, and details of the proposed installed equipment (location in the building, power ratings, specifications, etc.).
2.24. | Other equipment
3. | Other. Proposed by the Candidate / Participant. | The Candidate/Participant may supplement their Tender with the solutions that do not contradict the Specifications or are not assessed by the Public Entity (PE)
The price must match the price of part of the Facility of Supplement 2.1, document 1, worksheet 1
|  |  |  | Total (EUR, excl. VAT) | Total cost of the optimisation solutions (EUR excl. VAT). Cost of additional work or savings
REMARKS:
1. The Public Entity fills in the specifications, object data, and design task taking into account the specific features and purpose of the object part.
2. The Public Entity provides known special requirements and descriptions of objects, rooms, functional blocks, and infrastructure. If descriptions are not provided in the Public Entity tables, the Candidate/Participant must submit their tenders in accordance with applicable regulations, standards, and other legal acts.
3. The Candidate may propose and suggest possible optimisations (by suggesting to supplement the Specifications, justifying the benefits of the proposals and their impact on the price of the Tender).
4. Where possible and rational, the cost of creating a facility or other part of a building should be detailed by isolating individual parts or components of the building and specifying the anticipated cost of each respective part or component.

## 4. Development of buildings. Co
Supplement 2.1 document 3 "Technical requirements for the creation of headquarters"
| Project name | Development of a military campus infrastructure in Klaipėda district, Kairiai
| Facility | Kairiai military town
| Type of construction | New construction
| Annex to terms & conditions | Annex 2 Specifications
| Supplement | Supplement 2.1 document 3 "Technical requirements for the creation of headquarters"
| Supplement document (worksheet) | worksheet 4. Development of buildings. Construction
Item No. | Building part/ System/ Area | Description of special requirements for premises/areas (if applicable) | Headquarters No. 1
|  |  | Description of solutions proposed by the Candidate/Participant (reference to the annex of the Tender: Section, part, item of the Tender). | Cost of development of the solution proposed by the Candidate / Participant (EUR excl. VAT) | Possible optimisation proposed by the Candidate – additional solutions to those in the Specification (reference to the Tender document, section, paragraph, clause). Price (EUR excl. VAT) This section is to be completed only for the Initial Tender | REMARKS
| To be completed by the Public entity (PE). When submitting the Tender, the information “To be completed by the Candidate/Participant" may be suspplemented by the Candidate/Participant | to be filled by the Public Entity (if specific requirements are known and applied | to be completed by Candidate / Participant | to be completed by Candidate / Participant | To be completed by the candidate (only applicable for Initial Tender)
1. | Building structures and other elements
1.1. | Foundations | Foundations under supporting structures must be designed considering the loads, the nature of the load increase, and the foundation ground properties. The final decision on the type of foundation must be based on the results of engineering geological studies and a cost comparison of different foundation types. The Participant provides information on selected foundation type, including structures, insulation, and finishing materials etc.
1.2. | Plinth installation | Wall covers (by the type of coating) must be compatible with the room purpose, resistant to wet cleaning and, where necessary, to chemicals used for disinfection. The Participant provides information on plinth solutions, finishing materials etc.
1.3. | Load-bearing external walls, structures | 1. For rooms subject to stricter security requirements, the exterior walls must ensure increased security (e.g., for weapons, document storage, and other rooms). 2. The areas designated for soldier movement must be separated from the external building enclosures to protect the building façades and their external elements from accidental damage. If necessary, external wall cladding must be used, ensuring its acoustic properties. Colours and materials must be selected based on resistance to dirt, ease of cleaning, material aging, wear, and simplicity of maintenance. 3. The architecture of the building's facade must be simple (without intricate details). Facades must be easy to maintain and durable, with facade materials offering increased resistance to dirt and damage. Facade materials must be resistant to adverse climatic effects and urban pollution and/or biological materials (moss, mould, insects, rodents, bird droppings) et al). 4. When the perimeter fence of the military unit coincides with the building wall, the elements of this wall, which are up to 2.5 metres in height, must meet the requirements for a minimum of 2 burglary resistance ratings. If there are trees, buildings, or other objects near the fence that can be used to climb over it, the fence's resistance to intrusion score must be lowered by two points. 5. Wall covers (by the type of coating) must be compatible with the room purpose, resistant to wet cleaning and, where necessary, to chemicals used for disinfection. The Participant provides information on external wall solutions, including structures, insulation, and finishing layers etc.
1.4. | Non-load-bearing external walls, structures
1.5. | Slabs on the ground. | 1. Acoustic noise in shared areas must not exceed 85 dBA, in work offices and meeting rooms – up to 50 dBA, and in sleeping areas – up to 32 dBA. 2. In special rooms with a high or medium potential for liquid accumulation, a floor slope must be installed to allow liquids to drain into the sewage system. 3. Floor coverings must be suitable for their intended use based on the function of the rooms or spaces where they are installed. 4. The floors must be designed to withstand their own weight and operational loads, considering the intended purpose of the rooms. The participant provides information about the floor slab structure (insulation types, layers) etc.)
1.6. | Floor slabs between levels
1.7. | Roof | 1. Measures to prevent the formation of icicles must be provided; 2. The roof must be easy to maintain, with maintenance walkways and platforms installed. Access to the roof must be easy but restricted with safety measures to prevent unauthorized individuals from accessing it; 3. Water from the building’s roof must be drained in such a way that it does not damage the building’s structure, roads, sidewalks, adjacent buildings, or harm the environment, and is directed into the underground stormwater drainage system. The participant provides information about the roof structure, insulation types and layers, and finishes. Rainwater collection and drainage system, roof protective railings, walkways, protective grilles, snow-retaining grilles, fire escape ladders etc.
1.8. | Load-bearing internal walls | Wall covers (by the type of coating) must be compatible with the room purpose, resistant to wet cleaning and, where necessary, to chemicals used for disinfection. The Participant provides information on internal wall solutions, including structures, insulation, and finishing layers etc.
1.9. | Non-load-bearing internal walls | Wall covers (by the type of coating) must be compatible with the room purpose, resistant to wet cleaning and, where necessary, to chemicals used for disinfection. The Participant provides information on internal wall solutions, including structures, insulation, and finishing layers etc.
1.10. | Structural elements | The structure of the buildings must be durable enough to withstand the negative effects of rare and potentially dangerous events. The main criterion when choosing building materials is public safety and material durability. These materials must be used in such a way that they meet the requirements or are of better quality than those specified in the technical requirements of these Specifications. The Participant provides information on stairs, ramps, balconies, and loggia structures, including coatings etc.
1.11. | Partitions | The finishing of partitions can be minimal (for example, where allowed by the construction norms, walls can be left unplastered, painted, or impregnated), but must comply with the intended use of the rooms. Wall covers (by the type of coating) must be compatible with the room purpose, resistant to wet cleaning and, where necessary, to chemicals used for disinfection. Work offices in the administrative area (No. 1.7., 1,13, 1.21.) The walls and ceilings/floors must be made of perforated ceramic brick masonry of at least 200 mm thick, or metal sheets of at least 3 mm thick, or solid wood at least 120 mm thick, or perforated brick or block masonry of at least 250 mm thick, or solid silicate brick masonry of at least 120 mm thick or similar materials providing equivalent resistance to break-ins. The Participant provides information on Partition types, structures, finishes etc.
1.12. | Floor coverings and finishes. | The floors in sanitary rooms/ spaces/ areas must be non-slip, waterproof, easy to clean, resistant to the cleaning agents and disinfectants used, and must have a slope towards the water drainage channels for self-collection into the sewage system. Floor and stair surfaces must be non-slip, easy to clean, and resistant to the chemicals used for wet cleaning and disinfection. The Participant provides information on floor type, structures, finish. The main room groups are distinguished – corridors, halls, administrative rooms, service rooms, and technical auxiliary rooms etc.
1.13. | Wall finish | Design the facades of buildings, considering the purpose of the buildings, the cohesive architectural appearance of the area, and long-term durability. The interior wall finishes can be minimal (for example, where construction regulations allow, walls can be unplastered and painted or impregnated), but they must meet the room's intended use. Walls in building rooms may be impregnated with clear liquids or impregnating paints. The wall covering (according to the type of covering) must match the room’s purpose, be resistant to damp cleaning, and where necessary, resistant to chemicals used for disinfecting. Where walls are to be painted, they must be painted with eco-friendly paints. Walls may also be coated with other high-quality and suitable coverings matching the purpose of the room. In sanitary units, the walls must be covered with ceramic tiles, and the cabin walls must be elevated from the floor and made of chipboard (MDP) or laminated panels (HPL), both with an aluminium frame. The participant provides descriptions of wall construction types, frame infills, and finishes etc.
1.14. | Ceiling finishing | The ceiling finishing may be minimal, but it must comply with the intended use of the room. The Participant provides information on ceiling types, structures, finishes etc.
1.15. | External doors, windows, and showcases | Outdoors must be equipped with direct-acting electromagnetic valves. Where required by special regulations, protective metal grills should be installed, and access to windows from the exterior of the building should be restricted. The Participant provides information on windows, showcases, doors, gates, including sills, trims, fittings, drive mechanisms, micro-ventilation elements, and other installed components.
1.16. | Skylights | The Participant provides information on skylights, roof hatches, including trims, fittings, drive mechanisms, ventilation elements, and other installed components.
1.17. | Internal doors and windows | 1. Internal doors, depending on the purpose, security, and number of operating cycles – metal, plastic, aluminium, or wooden (veneered). Fittings must be adapted to the designated use of the premises. Entrance doors to security zones (electronic security system requirement rooms of types 4 and 5) must be equipped with direct-acting electromagnetic locks (without a free passage function), scanning devices, and, if required, intercom systems. Doors must be designed to provide sound insulation where required, withstand increased operational loads, and be easy to operate. Access control door exit from the indoors must also be provided with a handle; these doors must also be lockable with a mechanical lock. Access to designated zones (detailed in Supplement 2.1 "Building, Structure, and Territory Specifications") must be restricted. In high-traffic areas, doors must also be protected with galvanised steel plates covering up to half their height. In areas where specific architectural solutions are required for internal equipment, other protective measures may be proposed. Access to doors and movement zones must be protected from damage and accelerated material wear. Information plates must be installed on doors. Information plates must be installed on interior doors and at entrances to each floor’s rooms, allowing for easy modification of displayed information. The information to be specified on the arrows and information boards will be determined by the Public Entity. All internal doors must have locks controlled by keys. There must be a manual method to open the electric skis using a key in case they do not work. Work offices in the administrative area (No. 1.7, 1,13, 1.21) Doors must be equipped with at least two locks, one with a cylindrical core tested in accordance with standard 1303, meeting at least security class 4 requirements, and the other being a lever lock. Testing of both lock bodies must be carried out in accordance with standard 12209 and must meet at least Level 4 requirements. If the door contains glass, it must be tested according to standard 356 and meet resistance requirements of at least P5A or be covered with a protective film no thinner than 400 microns, and: 1) testing of door leaves and frames must be carried out in accordance with standard 1627 and must meet security requirements of at least RC classification or higher. 2) The door leaf must be made of profile steel. The pipe profile must be no thinner than 20 x 28 mm, with a wall thickness no thinner than 1.5 mm, and must be installed along the entire perimeter of the frame. The installation location of the lock is reinforced with a box made of pipe profile of at least 20 x 28 mm thick along the entire perimeter of the lock in the plane of the door. If the width of the leaf exceeds 800 mm, an additional support must be installed across the full height of the leaf. The gap between the door leaf and the frame must not exceed 6 mm. Stone wool infill no thinner than 28 mm. On the outer leaf side, a steel sheet, at least 1.5 mm thick, is placed on the tubular profiles. The sheet, no less than 12 mm, must cover the gap between the frame and the door leaf. A steel sheet, at least 1.5 mm thick, is attached to the inner side of the leaf frame. The frame is made of profile steel, with dimensions not smaller than 80 x 40 mm, and the wall thickness not less than 3 mm. The frame must be fixed at least at six points with metal rods or bolts with a diameter of no less than 14 mm, or masonry pins with a diameter of no less than 12 mm and a length of 150 mm. The gap between the frame and the wall, after inserting rods, must be filled with a cement mortar mixture. At least three metal pins with a diameter of no less than 12 mm and length of 15 mm must be installed on the hinge side. The Participant provides information on interior room windows, showcases, doors, gates, including sills, trims, fittings, drive mechanisms, and other installed components.
1.18. | Sun protection | External heat gain management must be planned by selecting equipment (devices) that limit direct sunlight from entering the rooms. They can be controlled mechanically when installed inside or be installed on the exterior of the window (room), in which case their control must be electric. The sun protection measures to be installed must be designed for increased operational load, as well as being easy and simple to maintain, with the ability to limit or even stop direct sunlight, while allowing diffuse light to pass through. The Participant provides information on roller blinds, awnings, and shutters, including drive mechanisms etc.
1.19. | Special built-in elements | Outdoor stair railings, handrails, joints, and covering elements must be installed from stainless steel pipes. Outdoor stair railings, handrails, joints, and covering elements must be made of stainless steel. The Participant provides information on grilles, railings, handrails, decorative and covering elements (light well covers, foot cleaning grates) et al).
1.20. | Other | Work offices in the administrative area (No. 1.7., 1,13, 1.21.) Grilles must be made of 45 x 6 mm steel flat bars, with a maximum spacing of 200 mm between them. Steel rods with a diameter of no less than 20 mm must be embedded into the bars every 150 mm. Opening grille fastening rods must be embedded in the wall to a depth of at least 200 mm. Swinging grilles must be locked with locks in at least two places, whose cylindrical cores must be tested according to standard 1303 and meet at least the requirements of security class 6; padlocks must be tested according to standard 12320 and must meet at least security level 6 requirements.
1.21. | Other. Proposed by the Candidate / Participant. | The Candidate / Participant may add to the Solution / Tender its own solutions that are not in conflict with the Specification or not evaluated by the Public Entity (PE)
2. | Building internal engineering systems
2.1. | Heating systems and equipment | It is necessary to install heat consumption metering. Measuring devices must have a continuous scanning function. The possibility of adapting the heating installation for the functional separation of the military unit facility must be planned, taking into account the ability to normalise the temperature in different areas and rooms of the military unit facility by location and time, as well as the momentary increase or loss of heat, separately measuring heat consumption in separated facilities, and smoothly adjusting parameters to ensure continuous adaptation to demand, including at different times of the day. Areas where underfloor heating will be installed must be planned in such a way that they do not interfere with future furniture attachment. The participant provides a description – heat supply, heating system, heat production, heating pipelines etc. Radiators, underfloor heating, radiant heating systems etc. Metering.
2.2. | Ventilation systems and equipment | Air conditioning must be installed in work offices and server rooms. In the server rooms and uninterrupted power supply room, a separate automated precision control air conditioning system must be provided. Separate electrical panels must be provided for air conditioning equipment, and a separate grounding loop must be provided for the equipment. A constant temperature of 20–25 °C and relative humidity of 40–55% must be maintained in these rooms. The conditioning system is duplicated: one working and the other backup units. The backup air conditioner must activate automatically by rotating if the temperature in the room increases or in the event of the main air conditioner failure; In the server rooms and uninterrupted power supply room, a separate ventilation system must be provided; engineering systems not directly related to these rooms should not be installed there. Rooms must be protected from water flooding. The Participant provides information on air supply and extraction units, with or without air treatment functionality, ventilation equipment, technical air system ventilation systems, ducts and pipelines, ventilation openings and grilles, cooling systems, ducts and pipelines.
2.3. | Cooling (air conditioning) systems and equipment | The components of the cooling system must have an anti-condensation insulating layer; Water cooling system distributors (cartridges, air conditioning pipe equipment, brackets) in accessible locations must have regulating and shut-off valves to allow for system operation and control; The system must be connected to the general control system of the military unit; To cool the server rooms, precision-controlled air conditioners must be installed, which operate at low outdoor temperatures, as well as an air supply and exhaust system connected to the building’s control system. It is recommended to assess the possibility of creating the necessary engineering solutions to recover/reuse heat emitted in server rooms. The Participant provides information on selected cooling (air conditioning) system and equipment.
2.4. | Water supply and sewage systems and equipment | Anywhere sound may be heard from the wastewater piping, low-noise – thick-walled piping must be used, which must be additionally insulated; The accessibility of revisions installed on the sewage stands and the cleaning of the sewage disposal network must be planned to be free and convenient. The Participant provides information on water supply pipelines, sanitary fixtures, filters, drinking water supply, metering etc.
2.5. | Water metering installation | It is necessary to install water consumption measurement devices with a remote reading function; To ensure the required water consumption rates and the fire water supply system needs, appropriate equipment must be selected and installed Main water supply pipelines to all Military Unit Objects must have separate meters and distribution. The Participant provides information on water metering etc.
2.6. | Cold water system | The water supply in the military unit's objects must be designed so that water is supplied to all collection points, taking into account the pressure, flow rate, water properties, and the purpose of the building's use, as well as peak water consumption at the same time. When different requirements are set for the parameters of the water used at the collection points, water can be supplied through independent pipelines or water supply systems, providing water with the required properties from the corresponding external water supply networks or systems, which appropriately prepare the water. Water supply and distribution must be sufficient and meet the requirements of hygiene standards and other legal acts. Water consumption metering devices with remote reading functionality must be installed. Separate metering must be installed for each system with different water consumption purposes. Sanitary equipment must be aesthetic, durable, modern, and suitable for the functional area in which it is installed, and must comply with sanitary requirements. Water must be supplied to the facilities by connecting them to the main water supply network. The equipment must be installed to ensure that the water consumption indicators for the building complex are no less than the standard values and that the fire protection water supply needs are met. If the supplied water quality is insufficient, it must be achieved through appropriate water treatment engineering solutions. The number of drinking water supply points must be determined in accordance with regulations and standards. The Participant provides information on the proposed cold water supply system.
2.7. | Hot water systems and equipment | 1. The water supply system must ensure that water is supplied to all water usage points according to pressure, flow rate, and water characteristics requirements, peak water consumption at one time, and the designated purpose of the Military unit’s facilities. It is necessary to install water consumption measurement devices with a remote reading function; To ensure the required water consumption rates and the fire water supply system needs, appropriate equipment must be selected and installed The Participant provides information on water supply pipelines, sanitary fixtures, filters, hot water supply, metering etc.
2.8. | Domestic wastewater systems and equipment | Wastewater must be collected and directed according to economically/technically justified solutions, issued technical conditions. Toilet pots must have a water barrier inside. Water to toilet cisterns must be supplied silently (quiet operation), using no more than 6 l / 3 l of water for flushing. Urinals must have a contactless tap. In all buildings, except for the barracks washbasins near the WC (or closest to them), contactless taps with temperature limiters must be installed, as well as solutions for legionella prevention or pipe cleaning, preventing stagnant water from forming in the pipes (especially at the furthest points/water taps). In the barracks, one of the four mixers must be contactless. All sanitary devices, drain receivers, faucets, and other plumbing fixtures must be certified according to the ISO 9000 series or equivalent standard and meet the sizes specified by EN standards, with CE marking. Plumbing appliances installed in the facility must meet the following general requirements: their interior and exterior must have a smooth, easily cleanable surface (all appliances can be made of stainless steel); they must not have sharp protruding parts (in the appliance and in the fixing details); washbasins must be equipped with chrome-plated metal siphons that match the colour of the water mixing taps and faucets; toilet bowls must be equipped with seats and covers made of durable plastic. The participant provides a description – wastewater pipelines, wastewater collection facilities, wastewater treatment facilities Wastewater treatment plants
2.9. | Surface water drainage, rainwater systems, and devices | Rainwater drainage from the structures must be ensured, collected, and channelled according to the issued sewage network connection conditions. The participant provides a description – wastewater pipelines, wastewater collection facilities, wastewater treatment facilities etc.
2.10. | Plumbing appliances | Sanitary equipment must be aesthetic, durable, modern, and suitable for the functional area in which it is installed, and must comply with sanitary requirements. Sanitary infrastructure must be equipped with soap dispensers, hand dryers, paper towel dispensers, toilet paper dispensers, and automatically switched on and off lights. The Participant provides information on sanitary appliances, equipment, and systems
2.11. | Other equipment | The Participant provides information on other equipment not included in the listed water supply and wastewater disposal systems.
2.12. | Electrical systems and equipment | Locations and movement paths with few users or where users are not always present must be equipped with occupancy sensors. This is particularly important in storage and inventory areas, as well as in places with low movement. The quality of the equipment and the thoughtful placement of occupancy detectors must ensure complete convenience, as the lights must always turn on and off at the required times. Artificial lighting must be coordinated with surveillance equipment spaces and arranged so as not to dazzle the video surveillance cameras. The private partner must aim to reduce the number of lighting source models used. All equipment must be accessible for cleaning and maintenance, especially in high locations. Outdoor lighting must be controlled from the room. The lighting of auxiliary rooms must be distributed according to functional zones, but the lighting of zones related to event functions must be centralized and controlled from a dedicated room. A sufficient power capacity three-phase power supply must be planned (for all planned equipment). The electrical networks of the buildings must be designed for all types (facades, territories, fire extinguishing equipment, local television networks, fire hydrant light indicators, safety signs, call systems, light enclosures). and others) to power the lighting. Electrical cable installation must comply with the technical requirements for this system’s installation. In the building's premises, all installed control and protection devices must have a label indicating the schematic dependency and purpose. There must be a label with the name of the recipients and the line's purpose in the internal part of the door panel, on the panel by the devices. The Participant provides information on high and/or medium voltage distribution equipment. Electric power generators, including cooling, exhaust gas and fuel supply systems, central battery and uninterruptible power supply equipment, and photovoltaic systems. Cables, wires, secondary distributors, routing systems, installation devices. Fixed lights, including electric lamps. Lightning protection, lightning rod, and grounding systems. Electricity metering.
2.13. | Security alarm systems and devices | The general requirements of the system are described in Suplement 2.1 document 36 "Requirements for Electronic Protection Systems"; The Participant provides information on protection alarm system and equipment.
2.14. | Access control systems and devices. | If card readers are installed outdoors, they must be mechanically sturdy and resistant to atmospheric conditions. In an emergency (power failure), control-operated doors must be unlockable with a key. The general requirements of the system are described in Suplement 2.1 document 36 "Requirements for Electronic Protection Systems". The Participant provides information on electromagnetic or mechanical locks. Access control system and devices.
2.15. | Video surveillance systems and equipment | The general requirements of the system are described in Suplement 2.1 document 36 "Requirements for Electronic Protection Systems". The Participant provides information on video surveillance cameras, video recording, storage, and display equipment.
2.16. | Computer and telephone networks | When designing telecommunications and computer networks and installing premises for primary equipment, the Cyber Defence Service of the Lithuanian Armed Forces (LK KGV ITT) must be provided with equipment room layouts, communication cables, networks, switching blocks, workstations, power and grounding system schemes in electronic format. When designing and constructing buildings and installing Equipment for Networks 1 and 2, representatives from the Cyber Defence Service of the Lithuanian Armed Forces (LK KGV ITT) must take part, in addition to other officials. The participant independently selects a communication provider required for PS needs and/or IP TV service provision. VS organizes the connection and service provision of the Ministry of Defence data transmission network. The Participant provides information on purpose of communication network, switch cabinet locations in the building, network switches, accessories, and other equipment.
2.17. | Automation systems and devices | A closed (local) building management system must be installed, allowing both monitoring and control of the main engineering system parameters. The accounting data analysis and processing software must be installed, designed for processing water, heat, electricity, and other meter data, generating reports, data analysis, and forecasting future needs. With the help of the installed systems, it must be possible to monitor and record the main microclimate parameters of at least five typical rooms (spaces). Meter readings must be transmitted automatically. The storage of copies of the transmitted telemetry data must be ensured. The Participant provides information on automated systems, control and monitoring devices, programming devices, sensors and actuators, communication intersection stations, and software for automated stations.
2.18. | Smoke extraction systems and equipment | The smoke extraction system and/or solution must be installed in accordance with the applicable regulations and standards. The Participant provides information on smoke extraction system, ducts, and equipment.
2.19. | Fire systems, fire detection systems, and equipment | The Participant provides information on fire detection and fire alarm systems.
2.20. | Fire extinguishing systems and equipment | The fire water supply system must comply with the applicable standards. The private partner must design an adequate number of external fire-fighting measures, considering the changes in the water supply system and fire safety standards. The private partner, considering the number of users in a specific Military Unit Object, must ensure appropriate evacuation conditions, ensuring that users can quickly and safely leave the danger zone or the area where a fire has occurred. Also, the appropriate structure, dimensions, and other technical fire safety measures must be ensured. The Participant provides information on fire suppression systems and devices.
2.21. | Gas pipeline system and equipment | The Participant provides information on gas pipeline networks, boilers, system and other equipment, metering.
2.22. | Specific use devices, other technological devices and systems | The Participant provides information on built-in elements for special purposes, signposts, informational and directional signs, colour-coded guidance systems, air compressors, liquid storage tanks etc.
2.23. | Renewable energy systems and devices are installed in the building. The system and equipment installed in the area are not evaluated here; such information is provided in the "Territory" worksheet before the field of engineering networks and systems. | The participant provides descriptions of systems and equipment, technical parameters, and details of the proposed installed equipment (location in the building, power ratings, specifications, etc.).
2.24. | Other equipment
3. | Other. Proposed by the Candidate / Participant. | The Candidate/Participant may supplement their Tender with the solutions that do not contradict the Specifications or are not assessed by the Public Entity (PE)
The price must match the price of part of the Facility of Supplement 2.1, document 1, worksheet 1
|  |  |  | Total (EUR, excl. VAT) | Total cost of the optimisation solutions (EUR excl. VAT). Cost of additional work or savings
REMARKS:
1. The Public Entity fills in the specifications, object data, and design task taking into account the specific features and purpose of the object part.
2. The Public Entity provides known special requirements and descriptions of objects, rooms, functional blocks, and infrastructure. If descriptions are not provided in the Public Entity tables, the Candidate/Participant must submit their tenders in accordance with applicable regulations, standards, and other legal acts.
3. The Candidate may propose and suggest possible optimisations (by suggesting to supplement the Specifications, justifying the benefits of the proposals and their impact on the price of the Tender).
4. Where possible and rational, the cost of creating a facility or other part of a building should be detailed by isolating individual parts or components of the building and specifying the anticipated cost of each respective part or component.