## 1. Creation of buildings. Needs
Supplement 2.1 document 7 "Technical requirements for the creation of an antenna field"
| Project name |  | Development of a military campus infrastructure in Klaipėda district, Kairiai
| Facility |  | Kairiai military town
| Type of construction |  | New construction
| Annex to terms & conditions |  | Annex 2 Specifications
| Supplement |  | Supplement 2.1 document 7 "Technical requirements for the creation of an antenna field"
| Supplement document (worksheet) |  | worksheet 1. Development of buildings. Needs
Item No. | The name of the room/space/functional block | Number of places | Phones connected to the KATT | Computer networks are connected to the unit's network 2 | Computer networks are connected to the KAS network 1 | Number of computerised workstations | Approximate area (sq. m) (if needed to determine) | The significance level of the room/space/functional block (A, B, C and D) | Description of special requirements for premises/areas (if applicable) | The area of the premises/space/functional block in square metres proposed by the Candidate/Participant | numbering of premises according to the explanations on the drawings proposed by the Candidate/Participant | Cost of development of the solution proposed by the Candidate / Participant (EUR excl. VAT) | Furniture/equipment inventory |  |  |  | Possible optimisation proposed by the Candidate – additional solutions to those in the Specification (reference to the Tender document, section, paragraph, clause). Price (EUR excl. VAT) This section is to be completed only for the Initial Tender | REMARKS
[13 empty] | Description of the building's furniture/equipment inventory needs and Special Requirements (if any) | The planned furniture/equipment inventory is purchased by *PS, **PS, or VS | The price of furniture and equipment proposed by the Candidate/Participant for the investor (which is purchased by the Private Entity) (*PS, **PS)) (EUR excl. VAT) | Cost for the installation of the furniture and equipment inventory proposed by the Candidate/Participant (*PS, **PS) (EUR excl. VAT)
| To be completed by the Public entity (PE). When submitting the Tender, the information “To be completed by the Candidate/Participant" may be suspplemented by the Candidate/Participant | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | to be completed by Candidate / Participant | to be completed by Candidate / Participant | to be completed by Candidate / Participant | To be completed by Public entity | To be completed by Public entity | to be completed by Candidate / Participant | to be completed by Candidate / Participant | To be completed by the candidate (only applicable for Initial Tender)
1. | Communication building
1.1. | Communication room
1.1.1. | Office | 2 | 2 | - | 2 | 2 | 12 | B | the walls and ceilings must be built of brick, blocks, or constructed from metal sheets, solid wood, or similar materials providing equivalent resistance to break-ins. The door leaf and frame must be made of metal sheets less than 2 mm thick, solid wood, particleboard, plywood, glass, or similar materials ensuring equivalent resistance to burglary. Doors must be equipped with one lock with a cylindrical core or a lever lock. Window frames must be made of durable material, and the glass must be coated with a protective film. Provide protective blinds on the windows. From each room, provide 6 channels, each with a minimum diameter of 50 mm, leading to the nearest tower. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 4 room. |  |  |  | Provide spaces for office furniture sets No. 2 – 2 pcs. (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | *PS
1.1.2. | Office | 1 | 1 | - | 1 | 1 | 8 | B |  |  |  |  | Provide spaces for office furniture sets No. 2 – 1 unit (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | *PS
1.1.3. | Office | 2 | 2 | - | 2 | 2 | 12 | B | The walls and ceilings must be built of brick, blocks, or constructed from metal sheets, solid wood, or similar materials providing equivalent resistance to break-ins. No windows are planned in the room. The rooms are arranged according to the resolution of the Government of the Republic of Lithuania dated 2018-08-13 No. 820 requirements. Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 4 room. |  |  |  | Provide spaces for office furniture sets No. 2 – 2 pcs. (according to document 28 of Supplement 2 of Annex 2.1 of the Terms) | *PS
1.2. | Building engineering system rooms
1.2.1. | Technical rooms | - | - | - | - | - | 8 | C | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 1 room. Video surveillance – general monitoring of building access points and entrances, Access control system – not planned.
1.2.2. | Electronic security systems switch room | - | - | - | - | - | 6 | A | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic security systems" Type 4 room.
1.2.3. | Switching room (communication distribution point) | - | - | - | - | - | 14 | A
1.3. | Other rooms
1.3.1. | San. Assembly | - | - | - | - | - | 2 | C | Magnetic contacts for the protective alarm system are planned on the operable parts of the building's exterior windows, assigned to the corridor area |  |  |  | Provide all equipment and furniture required for the room's functionality | PS
1.3.2. | Corridor | - | - | - | 1 | - | 36 | C | Security systems are installed in accordance with document 36 of Supplement 2.1 "Requirements for the installation of electronic protection systems" for type 1 room, Video surveillance – general monitoring of access to the building and building entrances inside the corridor, Access control system – planned at all external doors of the building In the room, 1 three-phase 380V socket 16A is planned. |  |  |  | Provide all equipment and furniture required for the room's functionality | PS
1.3.3. | Vestibule | - | - | - | 1 | - | 2 | C | In the room, 1 socket 230V is planned.
1.4. | Other. Proposed by the Candidate / Participant. | [7 empty] | The Candidate/Participant may supplement their Tender with the solutions that do not contradict the Specifications or are not assessed by the Public Entity (PE)
Total building area
The price must match the price of part of the Facility of Supplement 2.1, document 1, worksheet 1
[12 empty] | Total (EUR, excl. VAT) |  |  |  |  | Total cost of the optimisation solutions (EUR excl. VAT). Cost of additional work or savings
2. | Antenna field (yard)
2.1. | Antenna field yard | - | - | - | - | - | 36000 | C | Design a 60 x 60 m fenced yard. Number of traffic lanes for the access road – 2 pcs; not less than 3 m. The access road must be integrated into the general internal road network of the area. The access road and the parking lot (inside the antenna field) must be adapted for heavy wheeled transport equipment, with the ability to withstand a load of 10.5 t per axle.
2.2. | Antenna field fence | - | - | - | - | - | - | C | Detailed information is provided on sheet 3. Creation of buildings. Construction
2.3. | Other. Proposed by the Candidate / Participant. | [7 empty] | The Candidate/Participant may supplement their Tender with the solutions that do not contradict the Specifications or are not assessed by the Public Entity (PE)
The price must match the price of part of the Facility of Supplement 2.1, document 1, worksheet 1
[12 empty] | Total (EUR, excl. VAT) |  |  |  |  | Total cost of the optimisation solutions (EUR excl. VAT). Cost of additional work or savings
3. | Radio communication tower | [16 empty] | 2 units are designed.
3.1. | Radio communication tower | - | - | - | - | - | - | C | Building height from the ground surface – 29 m. The antenna mounting pole, i.e., a prefabricated steel structure building, designed for the mounting of telecommunications antennas at a specific height. The building's structure must be selected such that in the upper part (height from 22 m to 29 m), it can withstand loads of at least 800 kg, with load distribution of up to 8.0 m². Inside the tower, climbing ladders with safety rails must be provided to prevent falls. Cable ladders must be provided along the entire height. Calculations for the maximum permissible loads of the building must be included. Signal lights must be provided at the top of the tower.
3.2. | Other. Proposed by the Candidate / Participant. | [7 empty] | The Candidate/Participant may supplement their Tender with the solutions that do not contradict the Specifications or are not assessed by the Public Entity (PE)
The price must match the price of part of the Facility of Supplement 2.1, document 1, worksheet 1
[12 empty] | Total (EUR, excl. VAT) |  |  |  |  | Total cost of the optimisation solutions (EUR excl. VAT). Cost of additional work or savings
REMARKS:
1. The Public Entity fills in the specifications, object data, and design task taking into account the features and purpose of the object.
2. The Public Entity provides known special requirements and descriptions of objects, rooms, spaces, functional blocks, and infrastructure. If descriptions are not provided in the Public Entity tables, the Candidate/Participant must submit their tenders in accordance with applicable regulations, standards, and other legal acts.
3. The Candidate/Participant may propose and suggest possible optimisations in their solutions (by suggesting to supplement the Specifications, justifying the benefits of the proposals and their impact on the price of the Tender).
4. The Public Entity classifies rooms/ spaces/ functional blocks by significance levels into functional sector significance levels A, B, C, and D (Specifications section "Functional sectors").
5. The areas provided in the table are approximate and may change depending on the implementation of regulatory acts and the requirements of the Specifications.
6. The technological rooms must be equipped with an air conditioning system, ensuring the proper operating conditions for the equipment installed in these rooms. Parameters are selected according to the recommendations of computer network equipment manufacturers. Temperature deviations in the rooms must be automatically recorded in the Registration Tool.
7. The size of technological premises indicated in the table is approximate, it is adjusted by evaluating the planned equipment quantities to be installed. The size of the room must allow easy access to the switchgear cabinets and equipment maintenance.
10. Technological rooms should not be located beneath sanitary facilities or in other areas where there is a high risk of flooding.
11. If necessary to clarify the solutions, the Participant may add rows to their table.
12. * The PS must provide for a one-time furniture purchase and warranty maintenance for a period of 5 years
13 The PS must provide equipment/furniture that is mandatory (or necessary) for the proper functioning (use) of buildings/premises, in accordance with legal acts/regulations, the Private Entity’s solutions, etc., including their further technical maintenance throughout the entire Contract period

## 2. Development of buildings.
Supplement 2.1 document 7 "Technical requirements for the creation of an antenna field"
| Project name | Development of a military campus infrastructure in Klaipėda district, Kairiai
| Facility | Kairiai military town
| Type of construction | New construction
| Annex to terms & conditions | Annex 2 Specifications
| Supplement | Supplement 2.1 document 7 "Technical requirements for the creation of an antenna field"
| Supplement document (worksheet) | worksheet 2. Development of buildings. Construction
|  |  | Description of solutions proposed by the Candidate/Participant (reference to the annex of the Tender: Section, part, item of the Tender). | Cost of development of the solution proposed by the Candidate / Participant (EUR excl. VAT) | Possible optimisation proposed by the Candidate – additional solutions to those in the Specification (reference to the Tender document, section, paragraph, clause). Price (EUR excl. VAT) This section is to be completed only for the Initial Tender | REMARKS
| To be completed by the Public entity (PE). When submitting the Tender, the information “To be completed by the Candidate/Participant" may be suspplemented by the Candidate/Participant | to be filled by the Public Entity (if specific requirements are known and applied | to be completed by Candidate / Participant | to be completed by Candidate / Participant | To be completed by the candidate (only applicable for Initial Tender)
1. | Communication building structures and other elements
1.1. | Foundations | Foundations under supporting structures must be designed considering the loads, the nature of the load increase, and the foundation ground properties. The final decision on the type of foundation must be based on the results of engineering geological studies and a cost comparison of different foundation types. The Participant provides information on selected foundation type, including structures, insulation, and finishing materials etc.
1.2. | Plinth installation | Wall covers (by the type of coating) must be compatible with the room purpose, resistant to wet cleaning and, where necessary, to chemicals used for disinfection. The Participant provides information on plinth solutions, finishing materials etc.
1.3. | Load-bearing external walls, structures | The areas designated for soldier movement must be separated from the external building enclosures to protect the building façades and their external elements from accidental damage. If necessary, external wall cladding must be used, ensuring its acoustic properties. Colours and materials must be selected based on resistance to dirt, ease of cleaning, material aging, wear, and simplicity of maintenance. The architecture of the building's facade must be simple (without intricate details). Facades must be easy to maintain and durable, with facade materials offering increased resistance to dirt and damage. Facade materials must be resistant to adverse climatic effects and urban pollution and/or biological materials (moss, mould, insects, rodents, bird droppings) et al). Wall covers (by the type of coating) must be compatible with the room purpose, resistant to wet cleaning and, where necessary, to chemicals used for disinfection. Provide 2 openings on each side of the tower (a total of 4 pcs). The Participant provides information on external wall solutions, including structures, insulation, and finishing layers etc.
1.4. | Non-load-bearing external walls, structures
1.5. | Slabs on the ground. | 1. Floor coverings must be suitable for their intended use based on the function of the rooms or spaces where they are installed. 2. The floors must be designed to withstand their own weight and operational loads, considering the intended purpose of the rooms. The participant provides information about the floor slab structure (insulation types, layers) etc.)
1.6. | Floor slabs between levels
1.7. | Roof | Measures to prevent the formation of icicles must be provided; The roof must be easy to maintain, with maintenance walkways and platforms installed. Access to the roof must be easy but restricted with safety measures to prevent unauthorized individuals from accessing it. Water from the building’s roof must be drained in such a way that it does not damage the building’s structure, roads, sidewalks, adjacent buildings, or harm the environment, and is directed into the underground stormwater drainage system. Provide the possibility to access the roof from the interior of the building. Provide a 3 x 5 m light construction antenna mounting platform on the building's roof with secure access to it. It rises 20 cm from light metal structures, covered with 30 mm marine plywood, to which temporary antenna mounts can be drilled or screwed, and its surface cannot be metal. At least two separate pipes/channels with a diameter of at least 7 cm must be installed next to the platform for the routing of 6 antenna cables. The first communication channel must be routed to room No. 1, the second communication channel must be routed to room No. 2. 2. Waterproof 4 electrical network sockets 230V 16A each and 2 units must be provided. 380 V 16 A three-phase. Lockable ladders for roof access from the exterior of the building must be provided. The participant provides information about the roof structure, insulation types and layers, and finishes. Rainwater collection and drainage system, roof protective railings, walkways, protective grilles, snow-retaining grilles, fire escape ladders etc.
1.8. | Load-bearing internal walls | The wall covering (according to the type of covering) must match the room’s purpose, be resistant to damp cleaning, and where necessary, resistant to chemicals used for disinfecting. The Participant provides information on internal wall solutions, including structures, insulation, and finishing layers etc.
1.9. | Non-load-bearing internal walls | Wall covers (by the type of coating) must be compatible with the room purpose, resistant to wet cleaning and, where necessary, to chemicals used for disinfection. The Participant provides information on internal wall solutions, including structures, insulation, and finishing layers etc.
1.10. | Structural elements | The main criterion when choosing building materials is public safety and material durability. These materials must be used in such a way that they meet the requirements or are of better quality than those specified in the technical requirements of these Specifications. The Participant provides information on stairs, ramps, balconies, and loggia structures, including coatings etc.
1.11. | Partitions | The finishing of partitions can be minimal, in accordance with the intended use of the rooms. Wall covers (by the type of coating) must be compatible with the room purpose, resistant to wet cleaning and, where necessary, to chemicals used for disinfection. Work office in the administrative area. (No. 1.1.3. The walls and ceilings/floors must be made of perforated ceramic brick masonry of at least 200 mm thick, or metal sheets of at least 3 mm thick, or solid wood at least 120 mm thick, or perforated brick or block masonry of at least 250 mm thick, or solid silicate brick masonry of at least 120 mm thick or similar materials providing equivalent resistance to break-ins. The Participant provides information on Partition types, structures, finishes etc.
1.12. | Floor coverings and finishes. | The floors in sanitary rooms/ spaces/ areas must be non-slip, waterproof, easy to clean, resistant to the cleaning agents and disinfectants used, and must have a slope towards the water drainage channels for self-collection into the sewage system. Floor and stair surfaces must be non-slip, easy to clean, and resistant to the chemicals used for wet cleaning and disinfection. The Participant provides information on floor type, structures, finish. The main room groups are distinguished – corridors, halls, administrative rooms, service rooms, and technical auxiliary rooms etc.
1.13. | Wall finish | Design the facades of buildings, considering the purpose of the buildings, the cohesive architectural appearance of the area, and long-term durability. The interior wall finishes can be minimal but must meet the room's intended use. The wall covering (according to the type of covering) must match the room’s purpose, be resistant to damp cleaning, and where necessary, resistant to chemicals used for disinfecting. Where walls are to be painted, they must be painted with eco-friendly paints. Walls may also be coated with other high-quality and suitable coverings matching the purpose of the room. In sanitary units, the walls must be covered with ceramic tiles, and the cabin walls must be elevated from the floor and made of chipboard (MDP) or laminated panels (HPL), both with an aluminium frame. The participant provides descriptions of wall construction types, frame infills, and finishes etc.
1.14. | Ceiling finishing | The ceiling finishing may be minimal, but it must comply with the intended use of the room. The Participant provides information on ceiling types, structures, finishes etc.
1.15. | External doors, windows | Where required by special regulations, protective metal grills should be installed, and access to windows from the exterior of the building should be restricted. The Participant provides information on windows, doors, including sills, trims, fittings, drive mechanisms, micro-ventilation elements etc.
1.16. | Internal doors and windows | Internal doors, depending on the purpose, security, and number of operating cycles – metal, plastic, aluminium, or wooden (veneered). Fittings must be adapted to the designated use of the premises. The access control doors must be equipped with electromagnetic locks and scanning devices for interior exit control, and must include a door handle and, as needed, intercom devices. Doors must be designed to provide sound insulation where required, withstand increased operational loads, and be easy to operate. In high-traffic areas, doors must also be protected with galvanised steel plates covering up to half their height. Access to doors and movement zones must be protected from damage and accelerated material wear. Information plates must be installed on the doors, allowing for easy modification of displayed information. All internal doors must have locks controlled by keys. There must be a manual method to open the electric skis using a key in case they do not work. Work office in the administrative area. (No. 1.1.3.) Doors must be equipped with at least two locks, one with a cylindrical core tested in accordance with standard 1303, meeting at least security class 4 requirements, and the other being a lever lock. Testing of both lock bodies must be carried out in accordance with standard 12209 and must meet at least Level 4 requirements. If the door contains glass, it must be tested according to standard 356 and meet resistance requirements of at least P5A or be covered with a protective film no thinner than 400 microns, and: 1) testing of door leaves and frames must be carried out in accordance with standard 1627 and must meet security requirements of at least RC classification or higher. 2) The door leaf must be made of profile steel. The pipe profile must be no thinner than 20 x 28 mm, with a wall thickness no thinner than 1.5 mm, and must be installed along the entire perimeter of the frame. The installation location of the lock is reinforced with a box made of pipe profile of at least 20 x 28 mm thick along the entire perimeter of the lock in the plane of the door. If the width of the leaf exceeds 800 mm, an additional support must be installed across the full height of the leaf. The gap between the door leaf and the frame must not exceed 6 mm. Stone wool infill no thinner than 28 mm. On the outer leaf side, a steel sheet, at least 1.5 mm thick, is placed on the tubular profiles. The sheet, no less than 12 mm, must cover the gap between the frame and the door leaf. A steel sheet, at least 1.5 mm thick, is attached to the inner side of the leaf frame. The frame is made of profile steel, with dimensions not smaller than 80 x 40 mm, and the wall thickness not less than 3 mm. The frame must be fixed at least at six points with metal rods or bolts with a diameter of no less than 14 mm, or masonry pins with a diameter of no less than 12 mm and a length of 150 mm. The gap between the frame and the wall, after inserting rods, must be filled with a cement mortar mixture. At least three metal pins with a diameter of no less than 12 mm and length of 15 mm must be installed on the hinge side. The Participant provides information on interior room windows, showcases, doors, gates, including sills, trims, fittings, drive mechanisms, and other installed components.
1.17. | Sun protection | External heat gain management must be planned by selecting equipment (devices) that limit direct sunlight from entering the rooms. They can be controlled mechanically when installed inside or be installed on the exterior of the window (room), in which case their control must be electric. The sun protection measures to be installed must be designed for increased operational load, as well as being easy and simple to maintain, with the ability to limit or even stop direct sunlight, while allowing diffuse light to pass through. The Participant provides information on roller blinds, awnings, and shutters, including drive mechanisms etc.
1.18. | Special built-in elements | Outdoor stair railings, handrails, joints, and covering elements must be installed from stainless steel pipes. The Participant provides information on grilles, railings, handrails, decorative and covering elements (foot cleaning grates) et al).
1.19. | Other | Work office in the administrative area. (No. 1.1.3.) Grilles must be made of 45 x 6 mm steel flat bars, with a maximum spacing of 200 mm between them. Steel rods with a diameter of no less than 20 mm must be embedded into the bars every 150 mm. Opening grille fastening rods must be embedded in the wall to a depth of at least 200 mm. Swinging grilles must be locked with locks in at least two places, whose cylindrical cores must be tested according to standard 1303 and meet at least the requirements of security class 6; padlocks must be tested according to standard 12320 and must meet at least security level 6 requirements.
2. | Building internal engineering systems
2.1. | Heating systems and equipment | It is necessary to install heat consumption metering. Measuring devices must have a continuous scanning function. The possibility of adapting the heating installation for the functional separation of the military unit facility must be planned, taking into account the ability to normalise the temperature in different areas and rooms of the military unit facility by location and time, as well as the momentary increase or loss of heat, separately measuring heat consumption in separated facilities, and smoothly adjusting parameters to ensure continuous adaptation to demand, including at different times of the day. Areas where underfloor heating will be installed must be planned in such a way that they do not interfere with future furniture attachment. The participant provides a description – heat supply, heating system, heat production, heating pipelines etc. Radiators, underfloor heating, radiant heating systems etc. Metering.
2.2. | Ventilation systems and equipment | The rooms must be equipped with ventilation systems and devices. The Participant provides information on air supply and extraction units, with or without air treatment functionality, ventilation equipment, technical air system ventilation systems, ducts and pipelines, ventilation openings and grilles, cooling systems, ducts and pipelines.
2.3. | Cooling (air conditioning) systems and equipment | The components of the cooling system must have an anti-condensation insulating layer; Water cooling system distributors (cartridges, air conditioning pipe equipment, brackets) in accessible locations must have regulating and shut-off valves to allow for system operation and control; The system must be connected to the general control system of the military unit; The Participant provides information on selected cooling (air conditioning) system and equipment.
2.4. | Water supply and sewage systems and equipment | Anywhere sound may be heard from the wastewater piping, low-noise – thick-walled piping must be used, which must be additionally insulated; The accessibility of revisions installed on the sewage stands and the cleaning of the sewage disposal network must be planned to be free and convenient. The Participant provides information on water supply pipelines, sanitary fixtures, filters, drinking water supply, metering etc.
2.5. | Water metering installation | It is necessary to install water consumption measurement devices with a remote reading function; To ensure the required water consumption rates and the fire water supply system needs, appropriate equipment must be selected and installed Main water supply pipelines to all Military Unit Objects must have separate meters and distribution. The Participant provides information on water metering etc.
2.6. | Cold water system | The water supply in the military unit's objects must be designed so that water is supplied to all collection points, taking into account the pressure, flow rate, water properties, and the purpose of the building's use, as well as peak water consumption at the same time. Water consumption metering devices with remote reading functionality must be installed. Separate metering must be installed for each system with different water consumption purposes. Sanitary equipment must be aesthetic, durable, modern, and suitable for the functional area in which it is installed, and must comply with sanitary requirements. Water must be supplied to the facilities by connecting them to the main water supply network. The equipment must be installed to ensure that the water consumption indicators for the building complex are no less than the standard values and that the fire protection water supply needs are met. If the supplied water quality is insufficient, it must be achieved through appropriate water treatment engineering solutions. The Participant provides information on the proposed cold water supply system.
2.7. | Hot water systems and equipment | The water supply system must ensure that water is supplied to all water usage points according to pressure, flow rate, and water characteristics requirements, peak water consumption at one time, and the designated purpose of the Military unit’s facilities. It is necessary to install water consumption measurement devices with a remote reading function; The Participant provides information on the proposed hot water supply system.
2.8. | Domestic wastewater systems and equipment | Wastewater must be collected and directed according to economically/technically justified solutions, issued technical conditions. Toilet pots must have a water barrier inside. Water to toilet cisterns must be supplied silently (quiet operation), using no more than 6 l / 3 l of water for flushing. Urinals must have a contactless tap; Touchless faucets with temperature regulators, as well as solutions for Legionella prevention or pipe cleaning, which prevent the formation of stagnant water in pipes (especially at the furthest points/water taps), must be installed All sanitary devices, drain receivers, faucets, and other plumbing fixtures must be certified according to the ISO 9000 series or equivalent standard and meet the sizes specified by EN standards, with CE marking. Plumbing appliances installed in the facility must meet the following general requirements: their interior and exterior must have a smooth, easily cleanable surface (all appliances can be made of stainless steel); they must not have sharp protruding parts (in the appliance and in the fixing details); washbasins must be equipped with chrome-plated metal siphons that match the colour of the water mixing taps and faucets; toilet bowls must be equipped with seats and covers made of durable plastic. The participant provides a description – wastewater pipelines, wastewater collection facilities, wastewater treatment facilities Wastewater treatment plants
2.9. | Surface water drainage, rainwater systems, and devices | Rainwater drainage from the structures must be ensured, collected, and channelled according to the issued sewage network connection conditions. The participant provides a description – wastewater pipelines, wastewater collection facilities, wastewater treatment facilities etc.
2.10. | Plumbing appliances | Sanitary equipment must be aesthetic, durable, modern, and suitable for the functional area in which it is installed, and must comply with sanitary requirements. Sanitary infrastructure must be equipped with soap dispensers, hand dryers, paper towel dispensers, toilet paper dispensers, and automatically switched on and off lights. The Participant provides information on sanitary appliances, equipment, and systems
2.11. | Other equipment | The Participant provides information on other equipment not included in the listed water supply and wastewater disposal systems.
2.12. | Electrical systems and equipment | Locations and movement paths with few users or where users are not always present must be equipped with occupancy sensors. Artificial lighting must be coordinated with surveillance equipment spaces and arranged so as not to dazzle the video surveillance cameras. The private partner must aim to reduce the number of lighting source models used. All equipment must be accessible for cleaning and maintenance, especially in high locations. the outdoor lighting must be controlled from the room The lighting of auxiliary rooms must be distributed according to functional zones, but the lighting of zones related to event functions must be centralized and controlled from a dedicated room. A sufficient power capacity three-phase power supply must be planned (for all planned equipment). The electrical networks of the buildings must be designed for all types (facades, territories, fire extinguishing equipment, local television networks, fire hydrant light indicators, safety signs, call systems, light enclosures). and others) to power the lighting. Electrical connections are planned on the exterior wall of the building at the vehicle parking area 2 pcs. 380 V 16 A three-phase. The Participant provides information on high and/or medium voltage distribution equipment. Electric power generators, including cooling, exhaust gas and fuel supply systems, central battery and uninterruptible power supply equipment, and photovoltaic systems. Cables, wires, secondary distributors, routing systems, installation devices. Fixed lights, including electric lamps. Lightning protection, lightning rod, and grounding systems. Electricity metering.
2.13. | Security alarm systems and devices | The general requirements of the system are described in Suplement 2.1 document 36 "Requirements for Electronic Protection Systems"; The Participant provides information on protection alarm system and equipment.
2.14. | Access control systems and devices. | If card readers are installed outdoors, they must be mechanically sturdy and resistant to atmospheric conditions. In an emergency (power failure), control-operated doors must be unlockable with a key. The general requirements of the system are described in Suplement 2.1 document 36 "Requirements for Electronic Protection Systems". The Participant provides information on electromagnetic or mechanical locks. Access control system and devices.
2.15. | Video surveillance systems and equipment | The general requirements of the system are described in Suplement 2.1 document 36 "Requirements for Electronic Protection Systems". The Participant provides information on video surveillance cameras, video recording, storage, and display equipment.
2.16. | Computer and telephone networks | When designing telecommunications and computer networks and installing premises for primary equipment, the Cyber Defence Service of the Lithuanian Armed Forces (LK KGV ITT) must be provided with equipment room layouts, communication cables, networks, switching blocks, workstations, power and grounding system schemes in electronic format. When designing and constructing buildings and installing Equipment for Networks 1 and 2, representatives from the Cyber Defence Service of the Lithuanian Armed Forces (LK KGV ITT) must take part, in addition to other officials. The participant independently selects a communication provider required for PS needs and/or IP TV service provision. VS organizes the connection and service provision of the Ministry of Defence data transmission network. The Participant provides information on purpose of communication network, switch cabinet locations in the building, network switches, accessories, and other equipment.
2.17. | Automation systems and devices | A closed (local) building management system must be installed, allowing both monitoring and control of the main engineering system parameters. The accounting data analysis and processing software must be installed, designed for processing water, heat, electricity, and other meter data, generating reports, data analysis, and forecasting future needs. Meter readings must be transmitted automatically. The storage of copies of the transmitted telemetry data must be ensured. The Participant provides information on automated systems, control and monitoring devices, programming devices, sensors and actuators, communication intersection stations, and software for automated stations.
2.18. | Smoke extraction systems and equipment | The smoke extraction system and/or solution must be installed in accordance with the applicable regulations and standards. The Participant provides information on smoke extraction system, ducts, and equipment.
2.19. | Fire systems, fire detection systems, and equipment | The Participant provides information on fire detection and fire alarm systems.
2.20. | Fire extinguishing systems and equipment | The fire water supply system must comply with the applicable standards. The private partner must design an adequate number of external fire-fighting measures, considering the changes in the water supply system and fire safety standards. The private partner, considering the number of users in a specific Military Unit Object, must ensure appropriate evacuation conditions, ensuring that users can quickly and safely leave the danger zone or the area where a fire has occurred. Also, the appropriate structure, dimensions, and other technical fire safety measures must be ensured. The Participant provides information on fire suppression systems and devices.
2.21. | Gas pipeline system and equipment | The Participant provides information on gas pipeline networks, boilers, system and other equipment, metering.
2.22. | Specific use devices, other technological devices and systems | The Participant provides information on built-in elements for special purposes, signposts, informational and directional signs, colour-coded guidance systems, air compressors, liquid storage tanks etc.
2.23. | Renewable energy systems and devices are installed in the building. The system and equipment installed in the area are not evaluated here; such information is provided in the "Territory" worksheet before the field of engineering networks and systems. | The participant provides descriptions of systems and equipment, technical parameters, and details of the proposed installed equipment (location in the building, power ratings, specifications, etc.).
2.24. | Other equipment | 1. Earthing – required for the protection of electrical equipment and radio communication devices from potential excessive electrical surges 2. Sealed conduits for the routing of communication cables are planned and installed in the building's walls. 3. Connections (both ends) N-type male or female Attenuation at 100 MHz – 2.5 dB (1.8 times). Length not less than 50 meters or more. The antenna cable LMR 600-UF must be routed from the building's antenna cable distribution box to the tower's antenna cable distribution box. The cable must not hang outside. The part of the cable buried must be additionally insulated against external factors such as moisture.
3. | Other. Proposed by the Candidate / Participant. | The Candidate/Participant may supplement their Tender with the solutions that do not contradict the Specifications or are not assessed by the Public Entity (PE)
The price must match the price of part of the Facility of Supplement 2.1, document 1, worksheet 1
|  |  |  | Total (EUR, excl. VAT) | Total cost of the optimisation solutions (EUR excl. VAT). Cost of additional work or savings
REMARKS:
1. The Public Entity fills in the specifications, object data, and design task taking into account the specific features and purpose of the object part.
2. The Public Entity provides known special requirements and descriptions of objects, rooms, functional blocks, and infrastructure. If descriptions are not provided in the Public Entity tables, the Candidate/Participant must submit their tenders in accordance with applicable regulations, standards, and other legal acts.
3. The Candidate may propose and suggest possible optimisations (by suggesting to supplement the Specifications, justifying the benefits of the proposals and their impact on the price of the Tender).
4. Where possible and rational, the cost of creating a facility or other part of a building should be detailed by isolating individual parts or components of the building and specifying the anticipated cost of each respective part or component.

## 3. Development of buildings.
Supplement 2.1 document 7 "Technical requirements for the creation of an antenna field"
| Project name | Development of a military campus infrastructure in Klaipėda district, Kairiai
| Facility | Kairiai military town
| Type of construction | New construction
| Annex to terms & conditions | Annex 2 Specifications
| Supplement | Supplement 2.1 document 7 "Technical requirements for the creation of an antenna field"
| Supplement document (worksheet) | worksheet 3. Development of buildings. Construction
Item No. | Building part/ System/ Area | Description of special requirements for premises/areas (if applicable) | Description of solutions proposed by the Candidate/Participant (reference to the annex of the Tender: Section, part, item of the Tender). | Cost of development of the solution proposed by the Candidate / Participant (EUR excl. VAT) | Possible optimisation proposed by the Candidate – additional solutions to those in the Specification (reference to the Tender document, section, paragraph, clause). Price (EUR excl. VAT) This section is to be completed only for the Initial Tender | REMARKS
| To be completed by the Public entity (PE). When submitting the Tender, the information “To be completed by the Candidate/Participant" may be suspplemented by the Candidate/Participant | to be filled by the Public Entity (if specific requirements are known and applied | to be completed by Candidate / Participant | to be completed by Candidate / Participant | To be completed by the candidate (only applicable for Initial Tender)
1. | Antenna field
1.1. | Building structures and other elements
1.1.1. | Foundations and bases | The foundations of the fence and gates poles, separate concrete foundations for the poles (at least 50 cm x 50 cm, depth: 80 cm); Solid surface vehicle parking area, maximum load per axle of a wheeled vehicle up to 10.5 t; Install a solid surface access road 2.5 m x 2 lanes. With a load of 10.5 t per axle; The surface of the antenna field yard – grass, levelled with a slope not exceeding 4 degrees. The Participant provides information on selected foundation type, including structures etc.
1.1.2. | Fence construction | The fence construction consists of: fence posts, mesh wire fabric, V-shaped top, NATO barbed wire, and concrete foundations; post diameter ≥ 76 mm, wall thickness ≥ 4 mm, made of steel, corrosion-protected, V-shaped top also with diameter ≥ 76 mm, wall thickness ≥ 4 mm, made of steel, corrosion-protected, designed for NATO barbed wire, post spacing: 3.0 m, post bracing (at least every tenth section and where the direction changes); the wire mesh must be corrosion-protected, wire thickness – not less than 3.1 mm, maximum mesh width – 50 mm, depth: 50 cm, anchored in the ground 3 times between posts, secured with 4 tension wires (wire thickness: at least 4.2 mm) reaching to the lower edge of the V-shaped top; V-shaped top with 4 tension wires (wire thickness: at least 4.2 mm), designed to fit and allow for the attachment of NATO barbed wire; The NATO barbed wire diameter – 690 mm (concertina), size 3, X-shaped, hot-dip galvanized. Distance between wire blades: 1.5 cm, wire blade length: 2.2 cm. The participant provides information about the selected fence construction.
1.1.3. | Gate construction | Entrance gates (passage width: 5.0 m, height: 3.3 m) consist of two gates of the same size, adjustable hinges, gate posts, and NATO barbed wire; Gate wings (2 pcs) (opening angle not less than 90°), made of tubing (not less than 80 mm x 40 mm cross-section, wall thickness – not less than 4.0 mm). The interior of the gate is filled with vertical bars (at least 30 mm x 20 mm in diameter, with the distance between the bars ≤ 120 mm). Provision for the gate fixation at the bottom; The bolt for connecting the gate wings, drill holes locked with a padlock, each gate wing with anti-climb protection (plate width: 60 cm, height: 80 cm) made of sheet steel (thickness: no less than 2.0 mm); Padlocks (2 pcs.) with 5 keys and labelled keychains; Posts (2 pcs.), made of square tubing (at least 150 mm x 150 mm), with wall thickness not less than 6.3 mm, designed to support two gate wings, with connection to the wire mesh fence; Anti-climb protection between the gate posts in the form of a concrete strip (length: 6.0 m, width: 20.0 cm; height: 50 cm) with structural reinforcement); The participant provides information about the selected gate construction.
1.1.4. | Gate structure | Gate (passage width: 1.25 m, height: 3.3 m) the gate consists of doors, adjustable hinges, gate posts, and NATO barbed wire; opening angle: not less than 90°, made of square tubing (at least 80 mm x 40 mm, wall thickness: not less than 4.0 mm), filled with vertical bars (square tube: at least 30 mm x 20 mm), with the internal distance between the bars ≤ 120 mm, adjustable hinges, and the upper part as anti-climb protection with NATO barbed wire, reinforced with internal wire (type: short, blade length: 12 mm, blade width: 15 mm, distance between blades: 26 mm) Bolt and drill bits for padlock locking, anti-penetration (width: 60 cm, height: 80 cm), made of sheet steel (thickness: no less than 2.0 mm); padlocks (2 pcs.) with 5 keys and inscribed key rings; Door plate on the door (width: no less than 150 mm x 150 mm, weather-resistant), consisting of a replaceable frame, plaque holder, and transparent cover; The door panel is mounted on the hinge inside. The gate opening is controlled by access control.
1.1.5. | Other | Provision for communication cable entries and an underground communication route to the planned PBZ headquarters building. There must be no Facilities (buildings or vegetation) obstructing the SATCOM systems' radiation at a 60° horizontal angle as per Figure 3, and a 20° gradient angle as per.
2. | Building engineering systems
2.1. | Surface water drainage, rainwater systems, and devices | The solution must include rainwater collection and other surface water collection and diversion solutions. The participant provides a description – wastewater pipelines, collection facilities, treatment facilities etc.
2.2. | Electrical systems and equipment | The antenna field requires 1 pcs. 380V, 16A 1 unit for each tower and 1 unit for each antenna. 380V and 230V 16A Power connections to the building. Provision of grounding connections, with a resistance of 10 ohms or less. Provision of electrical inputs with outdoor electrical distribution cabinets. The participant provides a description of the electrical systems and equipment.
2.3. | Access control systems and devices. | Card readers installed outdoors near the gates must be mechanically robust and weather-resistant. In case of an emergency (power outage), the access control-controlled gates must be capable of being unlocked with a key. The Participant provides information on electromagnetic or mechanical locks. Access control system and devices.
2.4. | Lighting solutions | The entire antenna field must be illuminated with LED lights, providing an illumination level of 20 lux. Artificial lighting must be coordinated with surveillance equipment spaces and arranged so as not to dazzle the video surveillance cameras. The private partner must aim to reduce the number of lighting source models used. Outdoor lighting must be controlled from the communications building premises. The participant provides a description of lighting systems.
2.5. | Communication systems | IT and communication cables will be installed in pipes with inspection shafts for future maintenance and repair work. Protection against rodents and small animals entering must be ensured. The maximum length of a fiber optic cable with no less than 5 cores between the headquarters building and the antenna field must not exceed 500 m. If the distance is greater, to avoid signal loss, a relay with a repeater must be installed. The participant provides a description of the communication systems.
2.6. | Video surveillance systems and equipment | All entry points to the territory, the entire perimeter, and external access to the perimeter fence must be monitored by IP video cameras. Perimeter IP video cameras are installed no further than 50 m apart from each other and adjusted to monitor each other. The Participant provides information on video surveillance cameras, video recording, storage, and display devices.
2.7. | Other equipment | Mandatory lightning protection and grounding installation solutions must be provided.
3. | Other. Proposed by the Candidate / Participant. | The Candidate/Participant may supplement their Tender with the solutions that do not contradict the Specifications or are not assessed by the Public Entity (PE)
The price must match the price of part of the Facility of Supplement 2.1, document 1, worksheet 1
|  |  |  | Total (EUR, excl. VAT) | Total cost of the optimisation solutions (EUR excl. VAT). Cost of additional work or savings
2. | Radio communication tower |  |  |  |  | Two units are planned inside the antenna field.
2.1. | Building structures and other elements
2.1.1. | Foundations | Foundations under supporting structures must be designed considering the loads, the nature of the load increase, and the foundation ground properties. The solution on the type of foundation must be based on the results of engineering geological studies and a comparison of the costs of different foundation types. The Participant provides information on selected foundation type, including structures, insulation, and finishing materials etc.
2.1.2. | Structural elements | Building structure elements must be new (cannot be refurbished, restored, or used). A lightning rod must be installed on the top of the building. The lightning rod with a grounding system must be connected with a separate conductor. Climbing ladders with protective hoops must be installed. Protective hoops are installed up to a height of 26 m. Along the entire height of the building, next to the ladders, on both sides, open cable mounting (fixing) ladders at least 250 mm wide must be installed, with cross bars spaced at least every 1 m. Building structure elements must be hot-dip galvanized. The possibility of installing three platforms on each tower for two soldiers to stand on during antenna installation must be provided. (h – 20 m, h – 23; h – 26). The distance from the building to the radio communication towers should be between 2 to 5 m. The participant provides information on the selected communication tower construction.
2.2. | Building engineering systems
2.2.1. | Electrical systems and equipment | At the base of the building (1.5 m height), a metal, weather-resistant (IP-66 protection class or higher) locked electrical distribution panel with two C6A automatic circuit breakers fixed on a DIN rail inside must be provided. The participant provides a description of the electrical systems and equipment.
2.2.2. | Lighting solutions | The top of the building must be equipped with signal lights (two signal lamps with LED bulbs of no less than 11 W power). The lights must be connected to the automatic circuit breakers with weather-resistant copper cables. The participant provides a description of the lighting solutions.
2.2.3. | Communication systems | The participant provides a description of the communication system.
2.2.4. | Other equipment | The building must have a warranty of no less than 5 years. A grounding/lightning protection system must be installed next to the building. Grounding resistance – no greater than 4 Ω. The building must be connected to this grounding system with a grounding bar. An adapter for the attachment of a 0.6 m parabolic antenna must be installed at the top of the building. The diameter of the adapter tube is 90±2 mm, length 1.0 m, distance from the structure 200 mm.
2.3. | Other. Proposed by the Candidate / Participant. | The Candidate/Participant may supplement their Tender with the solutions that do not contradict the Specifications or are not assessed by the Public Entity (PE)
The price must match the price of part of the Facility of Supplement 2.1, document 1, worksheet 1
|  |  |  | Total (EUR, excl. VAT) | Total cost of the optimisation solutions (EUR excl. VAT). Cost of additional work or savings
REMARKS:
1. The Public Entity fills in the specifications, object data, and design task taking into account the specific features and purpose of the object part.
2. The Public Entity provides known special requirements and descriptions of objects, rooms, functional blocks, and infrastructure. If descriptions are not provided in the Public Entity tables, the Candidate/Participant must submit their tenders in accordance with applicable regulations, standards, and other legal acts.
3. The Candidate may propose and suggest possible optimisations (by suggesting to supplement the Specifications, justifying the benefits of the proposals and their impact on the price of the Tender).
4. Where possible and rational, the cost of creating a facility or other part of a building should be detailed by isolating individual parts or components of the building and specifying the anticipated cost of each respective part or component.