## 1. Creation of buildings. Needs
Supplement 2.1 document 8 "Technical requirements for the creation of a helicopter landing site"
| Project name |  | Development of a military campus infrastructure in Klaipėda district, Kairiai
| Facility |  | Kairiai military town
| Type of construction |  | New construction
| Annex to terms & conditions |  | Annex 2 Specifications
| Supplement |  | Supplement 2.1 document 8 "Technical requirements for the creation of a helicopter landing site"
| Supplement document (worksheet) |  | worksheet 1. Development of buildings. Needs
Item No. | The name of the room/space/functional block | Number of places | Phones connected to the KATT | Computer networks are connected to the unit's network 2 | Computer networks are connected to the KAS network 1 | Number of computerised workstations | Approximate area (sq. m) (if needed to determine) | The significance level of the room/space/functional block (A, B, C and D) | Description of special requirements for premises/areas (if applicable) | The area of the premises/space/functional block in square metres proposed by the Candidate/Participant | numbering of premises according to the explanations on the drawings proposed by the Candidate/Participant | Cost of development of the solution proposed by the Candidate / Participant (EUR excl. VAT) | Furniture/equipment inventory |  |  |  | Possible optimisation proposed by the Candidate – additional solutions to those in the Specification (reference to the Tender document, section, paragraph, clause). Price (EUR excl. VAT) This section is to be completed only for the Initial Tender | REMARKS
[13 empty] | Description of the building's furniture/equipment inventory needs and Special Requirements (if any) | The planned furniture/equipment inventory is purchased by *PS, **PS, or VS | The price of furniture and equipment proposed by the Candidate/Participant for the investor (which is purchased by the Private Entity) (*PS, **PS)) (EUR excl. VAT) | Cost for the installation of the furniture and equipment inventory proposed by the Candidate/Participant (*PS, **PS) (EUR excl. VAT)
| To be completed by the Public entity (PE). When submitting the Tender, the information “To be completed by the Candidate/Participant" may be suspplemented by the Candidate/Participant | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | To be completed by Public entity | to be completed by Candidate / Participant | to be completed by Candidate / Participant | to be completed by Candidate / Participant | To be completed by Public entity | To be completed by Public entity | to be completed by Candidate / Participant | to be completed by Candidate / Participant | To be completed by the candidate (only applicable for Initial Tender)
1. | Helipad (VFR type) | [7 empty] | *The helipad is planned to be monitored by video surveillance with at least 8 stationary video cameras (the exact number and installation locations will be coordinated during the design proposals stage). | [8 empty] | Two helicopter landing pads are to be designed.
1.1. | Parking and service area | - | - | - | - | - | 900 | B | The landing pad should be designed for flights according to standard visual flight rules in two directions. One (1) helicopter parking and service area should be provided. 30 x 30m. The maximum helicopter weight is 22,680 kg (on two axles and four wheels). |  |  |  | Provide all equipment required for the building's functionality | PS
1.2. | Side safety strip | - | - | - | - | - | 1125 | C | A hard surface side safety strip with a width of 7.5 m must be installed around the helicopter parking area on all sides. |  |  |  | Provide all equipment required for the building's functionality | PS
1.3. | Primary surface | - | - | - | - | - | 8100 | C | 1. The size of the helicopter primary surface is 90 x 90 m. The orientation of the helicopter take-off/landing zone on the horizontal plane (the primary take-off/landing direction) is selected considering the prevailing wind direction, terrain features, and the layout of existing buildings. 2. The safety zone and the landing pad height above ground level must be uniform
1.4. | Safety surface | - | - | - | - | - | 10800 | C | Immediately behind the helicopter primary surface begins the safety zone, its length is 120.0 m and its width is 90.0 m.
1.5. | Potential incident zone | - | - | - | - | - | 21600 | C | Beyond the safety zone begins the potential incident zone, its length is 240.0 m and its width is 90.0 m. The trapezoidal approach landing guidance surface starts immediately behind the primary surface 90,0 x 90,0 m. The approach landing guidance surface extends up to 45.0 m in height (horizontally 360.0 m) with slopes 8H:1V
1.6. | Other. Proposed by the Candidate / Participant. | [7 empty] | The Candidate / Participant may add to the Solution / Tender its own solutions that are not in conflict with the Specification or not evaluated by the Public Entity (PE)
The price must match the price of part of the Facility of Supplement 2.1, document 1, worksheet 1
[12 empty] | Total (EUR, excl. VAT) |  |  |  |  | Total cost of the optimisation solutions (EUR excl. VAT). Cost of additional work or savings
REMARKS:
1. The Public Entity fills in the specifications, object data, and design task taking into account the features and purpose of the object.
2. The Public Entity provides known special requirements and descriptions of objects, rooms, spaces, functional blocks, and infrastructure. If descriptions are not provided in the Public Entity tables, the Candidate/Participant must submit their tenders in accordance with applicable regulations, standards, and other legal acts.
3. The Candidate/Participant may propose and suggest possible optimisations in their solutions (by suggesting to supplement the Specifications, justifying the benefits of the proposals and their impact on the price of the Tender).
4. The Public Entity classifies rooms/ spaces/ functional blocks by significance levels into functional sector significance levels A, B, C, and D (Specifications section "Functional sectors").
5. The areas provided in the table are approximate and may change depending on the implementation of regulatory acts and the requirements of the Specifications.
6. The technological rooms must be equipped with an air conditioning system, ensuring the proper operating conditions for the equipment installed in these rooms. Parameters are selected according to the recommendations of computer network equipment manufacturers. Temperature deviations in the rooms must be automatically recorded in the Registration Tool.
7. The size of technological premises indicated in the table is approximate, it is adjusted by evaluating the planned equipment quantities to be installed. The size of the room must allow easy access to the switchgear cabinets and equipment maintenance.
10. Technological rooms should not be located beneath sanitary facilities or in other areas where there is a high risk of flooding.
11. If necessary to clarify the solutions, the Participant may add rows to their table.
12. * The PS must provide for a one-time furniture purchase and warranty maintenance for a period of 5 years
13 The PS must provide equipment/furniture that is mandatory (or necessary) for the proper functioning (use) of buildings/premises, in accordance with legal acts/regulations, the Private Entity’s solutions, etc., including their further technical maintenance throughout the entire Contract period

## 2. Development of buildings.
Supplement 2.1 document 8 "Technical requirements for the creation of a helicopter landing site"
| Project name | Development of a military campus infrastructure in Klaipėda district, Kairiai
| Facility | Kairiai military town
| Type of construction | New construction
| Annex to terms & conditions | Annex 2 Specifications
| Supplement | Supplement 2.1 document 8 "Technical requirements for the creation of a helicopter landing site"
| Supplement document (worksheet) | worksheet 2. Development of buildings. Construction
Item No. | Building part/ System/ Area | Description of special requirements for premises/areas (if applicable) | Description of solutions proposed by the Candidate/Participant (reference to the annex of the Tender: Section, part, item of the Tender). | Cost of development of the solution proposed by the Candidate / Participant (EUR excl. VAT) | Possible optimisation proposed by the Candidate – additional solutions to those in the Specification (reference to the Tender document, section, paragraph, clause). Price (EUR excl. VAT) This section is to be completed only for the Initial Tender | REMARKS
| To be completed by the Public entity (PE). When submitting the Tender, the information “To be completed by the Candidate/Participant" may be suspplemented by the Candidate/Participant | to be filled by the Public Entity (if specific requirements are known and applied | to be completed by Candidate / Participant | to be completed by Candidate / Participant | To be completed by the candidate (only applicable for Initial Tender)
| Helipad |  |  |  |  | Two helicopter landing pads are to be designed
1. | Building structures and other elements
1.1. | Foundations and bases | Foundations under supporting structures must be designed considering the loads, the nature of the load increase, and the foundation ground properties. The final decision on the type of foundation must be based on the results of engineering geological studies and a cost comparison of different foundation types. The Participant provides information on selected foundation type, including structures etc.
1.2. | Building structure | 1. The surface of the landing pad is concrete; 2. the surface classification number (hereinafter – PCN, Pavement Classification Number) no less than 20; 3. the surface slopes – from 1% to 1.5%; 4. at the edges, there must be 7.5 m wide asphalt side safety strips 5. The slopes and other parameters of the helicopter landing pads are designed according to NATO Standard AATMP-38 and LKS STANAG 7114 and LKS STANAG 7174 requirements; The participant provides information about the selected helicopter landing pad construction.
1.3. | Other | 1. The maximum single-wheel TP load per axis is up to 10.5 t; 2. access should be provided by a hard surface, integrated into the overall military area road network. 3. The width of the designed road is 6.0 m (2 traffic lanes of 3.0 m each), and the width of the shoulders is 1.0 m; 4. A road for refuelling vehicles with a parking (turnaround) area is planned next to the landing pad.
2. | Building engineering systems
2.1. | Surface water drainage, rainwater systems, and devices | The helicopter landing pad must be designed with a drainage system for collecting and removing rainwater. The participant provides a description – wastewater pipelines, collection facilities, treatment facilities etc.
2.2. | Electrical systems and equipment | It is planned that the entire control of the helicopter landing pad lighting, signal light system, and wind vane lighting will be possible from the PBZ operator's room; The participant provides a description of the electrical systems and equipment.
2.3. | Lighting solutions | 1. A control system for signal and perimeter lights must be designed; 2. A signal light control system must be designed for the helicopter landing pad, consisting of a lighting system controller (AVS), perimeter lights, direction indicator lights, obstacle lights, wind vane, and helicopter approach indicator; 3. A backup, uninterrupted power supply for the lighting systems must be provided for no less than a 24-hour period. A diesel generator is planned for uninterrupted power supply. The participant provides a description of lighting systems.
2.4. | Security alarm systems and devices | No need.
2.5. | Video surveillance systems and equipment | The general requirements of the system are described in Suplement 2.1 document 36 "Requirements for Electronic Protection Systems". The Participant provides information on video surveillance cameras, video recording, storage, and display equipment.
2.5. | Other equipment | 1. A grounding point must be provided at the landing pad, with a grounding resistance of up to 10 ohms; 2. Surface markings with daytime markings and a signal light system must be provided at the landing pad; 3. The installation of a wind vane with lighting, complying with ICAO requirements, must be planned; 4. Oil product catch basins must be provided at the landing pad in case of an emergency; 5. Lightning protection installation must be planned; 6. Marking of obstacles near the landing pad with lights or daytime markings must be planned; 7. The centre of the pad must be marked with the letter "H" in white; 8. All project proposals agreed with the user must also be coordinated with the Lithuanian Armed Forces Lithuanian Military Aviation Administration; 9. It must be required that after completing the construction works, a PCN (PCR) measurement must be carried out by a certified company according to ICAO requirements; 10. The marking and lighting of the helicopter landing pads must be designed according to NATO Standard AATMP-12 and LKS STANAG 3619.
3. | Other. Proposed by the Candidate / Participant. | The Candidate/Participant may supplement their Tender with the solutions that do not contradict the Specifications or are not assessed by the Public Entity (PE)
The price must match the price of part of the Facility of Supplement 2.1, document 1, worksheet 1
|  |  |  | Total (EUR, excl. VAT) | Total cost of the optimisation solutions (EUR excl. VAT). Cost of additional work or savings
REMARKS:
1. The Public Entity fills in the specifications, object data, and design task taking into account the specific features and purpose of the object part.
2. The Public Entity provides known special requirements and descriptions of objects, rooms, functional blocks, and infrastructure. If descriptions are not provided in the Public Entity tables, the Candidate/Participant must submit their tenders in accordance with applicable regulations, standards, and other legal acts.
3. The Candidate may propose and suggest possible optimisations (by suggesting to supplement the Specifications, justifying the benefits of the proposals and their impact on the price of the Tender).
4. Where possible and rational, the cost of creating a facility or other part of a building should be detailed by isolating individual parts or components of the building and specifying the anticipated cost of each respective part or component.