DĖL ATSAKYMO Į GAUTĄ PAKLAUSIMĄ PATEIKIMO /

ON SUBMITTING A RESPONSE TO AN ENQUIRY RECEIVED

| Nr No | Klausimas / Question | Atsakymas / Answer |
| --- | --- | --- |
|  | Lietuvių kalba: „klausimas dėl techninės specifikacijos 1.9 3. punkto. Yra minima, kad "Maksimali elektros galia kurios pastatas reikalauja vienu metu, kai veikia visi svarbiausi įrenginiai yra XX kW". Galingumas nurodomais skirtingas visuose objektuose. Ar šiuo punktu norima paminėti, kad projektuojama sistema turėtų palaikyti objektą 1.9 3. punkte nurodytu galingumu elektros dingimo atveju?“ Translation in English: Question concerning point 1.9 3 of the technical specification. It mentions that "The maximum electrical power that the building requires at one time, when all the most important devices are operating, is XX kW". The power ratings are different for each facility. Is this point meant to imply that the system to be designed should support the facility at the power specified in 1.9(3) in the event of a power outage?" | Lietuvių kalba: Techninėje specifikacijoje nurodyta pastato „Maksimali elektros galia, kurios pastatas reikalauja vienu metu, kai veikia visi svarbiausi įrenginiai, yra XX kW“ pateikta kaip orientacinė informacija, skirta bendrajam supratimui ir galimų pastato naudotojo poreikių įvertinimui. Ši reikšmė padeda suprasti maksimalų galimą elektros energijos poreikį, tačiau tai nereiškia, kad tiek galingumo visais atvejais turėtų palaikyti autonominė sistema elektros dingimo metu. Elektros tiekimo sutrikimo atveju sistema turi palaikyti tuo metu esantį elektros energijos poreikį tik tiek, kiek tai leidžia techninėje specifikacijoje numatytų komponentų (saulės modulių, akumuliatorių ir kitos įrangos) galingumai bei esamos aplinkybės – paros metas (diena/naktis), oro sąlygos (saulėta ar apsiniaukę), akumuliatorių įkrovimo lygis ir pan. Svarbu suprasti, kad veikiant visiems įrenginiams maksimaliu režimu, elektros energijos rezervai gali būti greitai išeikvojami, todėl vartotojams gali reikėti valdyti elektros vartojimą pagal esamą situaciją ir sistemos galimybes. Translation in English: The Technical Specification's reference to the building's “The maximum electrical power that the building requires at one time, when all the most important devices are operating, is XX kW” is provided as indicative information for general understanding and assessment of the possible needs of the building user. This value helps to understand what the maximum demand for electricity may be, but it does not mean that the autonomous system should always support this much power during a power outage. In the event of a power outage, the system must support the current demand for electricity only to the extent allowed by the capacities of the components (solar modules, batteries and other equipment) specified in the technical specification and the current circumstances - time of day (day/night), weather conditions (sunny or cloudy), battery charge level, etc. It is important to understand that when all devices are operating at maximum mode, electrical energy reserves can be quickly depleted, so users may need to manage electricity consumption according to the current situation and system capabilities. |

Su pagarba,

Komisija

/

Sincerely,

Commission