## Cover
INTERFACE CONTROL FORM
PARTICULAR INTERFACES BETWEEN ENE AND INF FOR KAUNAS INFRASTRUCTURE MAINTENANCE FACILITY (ICF_203) ENE - FAC
RBDL-DII-OS8170-EE_LO-ICF-E-00001
[5 empty] | Revision: | 0.01
[5 empty] | Author: | Dmitrijs Kilups
[5 empty] | Date: | 2025-06-16
The sole responsibility of this publication lies with the author. The European Union is not responsible for any use that may be made of the information contained therein.
Ownership
Document Owner |  |  |  | RB Rail - System Engineering and Assurance Department
Approved by |  |  |  |  | Decision No. |  |  | Date
Version History
Rev | Version | Date | Author |  | Issue purpose |  | Description of changes
| 0.01 | 2025-06-16 | D. Kilups |  | Initial revision prepared |  | First Issue

## Guideline
Guideline about how to fill in the next sheets
This document is an Interface Control Form. Its aim is to collect: - Interface Requirements Specification -> this implies not only the definiiton of requirements itself, but also the information about which requirements apply to which (specific) objects/assets in the RBGP. - Requirements Implementation and Resolution information -> which actors are involved in the Interface Process from identification up to validation. - Requirements Management Information -> for Interface Managers to ensure that requirements are implemented in the right "objects". Please, notice that as long as dealing with requirements and while the RBR official tool for requirements management is not in place, this ICF substitutes and covers the Requirements process.
Sheet Name | Purpose
Cover | Official page of RB Rail Documents
Acronisms & Definitions | Official page of RB Rail Documents
Interface Description | Page to be filled in at Identification/Definition phase by Responsible Entity and Interface Experts (RBR or IBs). This sheet describes the Interface, the Entities involved in the Identification phase and a prior assignement of responsibilities for the rest of the project lifecycle. Let's insist that this is a prior assignement of responsibilities, the History of responsible entities that have finally implemented the ICF will be recorded in the ICF Approval sheet.
ICF Approval | Page to be filled in by Interface Experts from RBR or the IBs. One block identifying Responsible Entity/Supporting Entity/Owner has to be filled in with every new contract/actor entering the project until covering the implementation phase (up to subsystem validation and prior to system integration and validation).
Requirements "AssetX - DisciplineX" (Replace the whole name between quotations by Asset or Discipline name of the requirements, for example: "Requirements Bridge" or "Requirements Track". | In this page, there is one part to be filled in by Responsible and Supporting Entities, and a second part to be filled in by Interface Experts. On the one side, Responsible Entity will propose the requirements to be then approved by RBR and the Supporting Entity. On the other side, Interface Experts together with each Consultant will complete the part dedicated to the agreement reached between parties about requirements (whther accepted or rejected, the implementation phase in case accepted, or rejection reasons and next steps in case rejected). The excel file attached on the right column, "INFRA_GENERIC_REQUIREMENTS" contains typical requirements applicable to the alignement/connection ML - ML and ML - Facilities. For Entities involved in the definition of these two types of ICFs, please use the file as support/reference. HOW TO USE : - Name the sheets according to the sheets in the file (replace the text "Requirements AssetS-Discipline". - Copy the applicable requirements from the attachment to your ICF file, analyze the requirements proposed and customize the requirement if needed. IMPORTANT: If you use the same requirement several times, in order not to repeat the requirement ID, modify it in the following way: - RequirementIDProposed-01 - RequirementIDProposed-02 ... - RequirementIDProposed-0n and so on. | INFRA GENERIC REQUIREMENTS
Requirements … | Use as many Requirements Sheets as you consider, to sort requirements out per disciplines or asset types (grouping criteria suggested).
References | Official page of RB Rail Documents

## Acronisms & Definitions
Acronyms and Abbreviations
A full list of acronyms and abbreviations can be found in RBR Glossary of Abbreviations. The following acronyms and abbreviations are used throughout this document:
Abbreviation | Definition
CCS | Rail Baltica Control Command and Signalling subsystem deployment
ENE | Rail Baltica Energy subsystem deployment
FAC | Facility
ICF | Interface Control Form
IM | Infrastructure Manager
INFRA | Infrastructure related to the civil infrastructure assets of Rail Baltica Project
NTPS | Non-traction power supply
RBGP | Rail Baltica Global Project
RBR | RB Rail AS
RU | Railway Undertaking
Definitions
The following terms are used throughout this document:
Term | Definition
D&B Contractor | Design and Build (Construction) Contractor for the subsystem
DTD Consultant | Design Contractor for the subsystem (both in MD and DTD)
Build Contractor | Construction Contractor for the subsystem
FAC DTD Consultant | Design Contractor for the IMF (both in MD and DTD)

## Interface Description
INTERFACE DESCRIPTION
This sheet describes the Interface at Identification Phase, including the Entities involved in the Identification together with the prior assignement of responsibilities for the rest of the project lifecycle. Again this is a prior assignement of responsibilities, the final responsible entities involved is recorded together with their signatures, in the ICF Approval sheet.
Interface Parameters | Value
Short Interface Description | INTERFACES BETWEEN ENE AND INF FOR KAUNAS INFRASTRUCTURE MAINTENANCE FACILITY
Interface Type | Generic
Interface Level | Level 1 (L1) - ICF between subsystems in the Railways System
Asset/s 1 (AssetID in PBS) | 2 ENE (200000000)
Asset/s 2 (AssetID in PBS) | 3.3 Local Facilities (303000000)
Owner of the Interface | RBR (on behalf of the Infrastructure Manager)
IDENTIFICATION PHASE
Entities Involved | Role | Stage in the Process
ENE Engineer (RB Rail) | Responsible Entity | Concept Design
FAC DTD Consultant | Supporting Entity | Master Design
RBR | Owner of the Interface
DESIGN (I) - MD, DTD, CONSTRUCTION
[DTD Consultant, FAC D&B Contractor, CCS or ENE Engineer, CCS or ENE D&B Contractor, Shadow Operator (on behalf of RU)] | Responsible Entity
[DTD Consultant, FAC D&B Contractor, CCS or ENE Engineer, CCS or ENE D&B Contractor, Shadow Operator (on behalf of RU)] | Supporting Entity
CONSTRUCTION/MANUFACTURE/INSTALLATION
Responsible Entity
Supporting Entity
SYSTEM INTEGRATION & VALIDATION (Test and Commissioning)
Responsible Entity
Supporting Entity

## ICF Approval
INTERFACE DEVELOPMENT and APPROVAL
This sheet describes the history of the Entities finally involved in the ICF lifecycle: Identification, Implementation (Design, Verification, Manufacture/Installation/Construction up to subsystem Integration and Validation), prior to System Integration and Validation. Every new contract signed implies a new entry in this sheet, implies an approval/rejection of the requirements specified.
IDENTIFICATION&DEFINITION PHASE
Entities | Actor | Stage in the Process (of the Entity) | Company | Approver Name | ICF Revision | Date
Responsible Entity | ENE Engineer | Concept Design | Joint Venture ITALFERR, IDOM, DB Engineering & Consulting GmbH | Uģis Sabulis/ RBR ENE Project Manager
Supporting Entity | [DTD Consultant, FAC D&B Contractor, CCS or ENE Engineer, CCS or ENE D&B Contractor, Shadow Operator (on behalf of RU)] | [For DTD Consultant stages are MD OR DTD For FAC D&B Contractor stages are MD, DTD or Construction For CCS Engineer stage is Concept For CCS&ENE D&B Contractor, stages are Generic Design, Application or MD and DTD For Shadow Operator stage is Concept]
Owner | RB RAIL (on behalf of Infrastructure Manager)
Deliverables used to create this ICF | Main Line Design version used (if applicable, provide link in PW): Facilities Design version used (if applicable, provide link in PW): CRS sheet (if applicable, provide link in PW): Feel free to add any other input/link used
Conclusions / Additional information | " Conclusion of the review of both designs is that there are still unresolved connection points…" (feel free to add some final statement).
REPEAT THE NEXT BLOCK WITH EVERY NEW CONTRACT SIGNED
XXXXXX PHASE
Entities Involved | Role | Stage in the Process (of the Entity) | Company | Approver Name |  | Signature / Date
Responsible Entity | [DTD Consultant, FAC D&B Contractor, CCS or ENE Engineer, CCS or ENE D&B Contractor, Shadow Operator (on behalf of RU)] | [For DTD Consultant stages are MD OR DTD For FAC D&B Contractor stages are MD, DTD or Construction For CCS Engineer stage is Concept For CCS&ENE D&B Contractor, stages are Generic Design, Application or MD and DTD For Shadow Operator stage is Concept]
Supporting Entity | [DTD Consultant, FAC D&B Contractor, CCS or ENE Engineer, CCS or ENE D&B Contractor, Shadow Operator (on behalf of RU)] | [For DTD Consultant stages are MD OR DTD For FAC D&B Contractor stages are MD, DTD or Construction For CCS Engineer stage is Concept For CCS&ENE D&B Contractor, stages are Generic Design, Application or MD and DTD For Shadow Operator stage is Concept]
Owner | RB RAIL (on behalf of IM) System Integration Engineer (on behalf of RBR)
Deliverables used to create this ICF | Main Line Design version used (if applicable, provide link in PW) Facilities Design version used (if applicable, provide link in PW) CRS sheet (if applicable, provide link in PW) Feel free to add any other imput/link used
Conclusions / Additional information | " Conclusion of the review of both designs is that there are still unresolved connection points…" (feel free to add some final statement).

## Requirements OCS foundations
Guideline: Area to be filled in by Interface Expert (RBR or IBs)
REQUIREMENTS SPECIFICATION |  |  |  |  | SOLUTION DETAILS (iSOLUTION DETAILS (optional - to be used if needed)f any) | [5 empty] | Left: Area for Responsible and Supporting Entities Right: Area for IF Expert (RBR/IB) | AGREEMENT ON REQUIREMENTS' IMPLEMENTATION AND PHASE IN WHICH WILL BE IMPLEMENTED
REQUIREMENTS APPLICABLE TO BOTH ENTITIES |  | Type of requirement | REFERENCE TO PARENT REQUIREMENTS (DESIGN GUIDELINES, ICF, STANDARDS ETC..) |  | Entity proposer of the solution (optional - support columns for the requirements discussion RE-SE) | Solution Proposed (optional - support columns for the requirements discussion RE-SE) | SCOPE SPLIT |  | Implementation Status (Connection OK, Connection NOK, Unknown) | Details of Implementation status (if NOT OK) |  | Interfacing Assets |  | Location [BP, Construction Object, Track Object] | Responsible Entity |  |  |  |  | Supporting Entity
|  | Generic/Specific | Document Number of Generic ICF and/or Design Guideline | Document Revision |  |  | Scope for Responsible Entity | Scope for Supporting Entity |  |  |  | Asset Type / Discipline [Funct.Class name] | Site ID / Connection Point - interfacing assets |  | Requirement ID + source | Status Applicable/Not applicable/ Implemented/Rejected/Accepted but not implemented/Under discussion/ | Phase to be Implemented (if Accepted) | Reasons for Rejection (if Rejected) | Decision/Comments Filled in by RE IF Expert | Requirement ID + source | Status (Requirement Accepted/Rejected, Not applicable Implemented,Accepted but not implemented/Under discussion) | Phase to be Implemented (if Accepted) | Reasons for Rejection (if Rejected) | Decision/Comments Filled in by SE Expert
Requirement ID - 001 In the area of facility tracks the space reservation for future electrificaion shall be procvided. The reservation shall be made based on the typical solutions in figure 1. The locations of OCS space reservation (No.'s of tracks) shall be agreed between RBR and IB. | [14 empty] | Requirement ID - 001 | Accepted |  |  |  | Requirement ID - 001
Figure 1 | [11 empty] | - | - | - | - | - | - | - | - | -
Requirement ID - 002 According to the local construction regulations in each of the Baltic Countries there are requirements for minimum horizontal and vertical distances between buried underground utilities, overhead utilities and structures. The ENE D&B Contractor shall consider the position of all external utilities (including existing) in FACC DTD Consultant’s design for the location of OCS poles in order to comply with requirements of local regulations for the distances between utilities and structures, as well as requirements providd in RB Rail Design Guidelines and Technical Specification for Construction. | [14 empty] | Requirement ID - 002 | Accepted |  |  |  | Requirement ID - 002
SCOPE SPLIT - REQUIREMENTS APPLICABLE TO ONE ENTITY
Responsible Entity of the Implementation | Supporting Entity of the Implementation
Requirements for the Design | [10 empty] | Left: Area for Responsible and Supporting Entities Right: Area for IF Expert (RBR/IB)
Requirement ID - 003 The ENE D&B Contractor must design OCS and location of OCS pole foundations; | [14 empty] | Requirement ID - 003 | Accepted |  |  |  | Requirement ID - 003
| Requirement ID - 004 The FAC DTD Consultant must reserve space for installatio of OCS poles in case of future electrification of depot. | [13 empty] | Requirement ID - 004 | Not applicable |  |  |  | Requirement ID - 004
Requirement ID - 005 The ENE D&B Contractor must develop OCS pole installation design using FAC DTD Consultant design as input, considering indicated loads and positions of fixation bolts, and in accordance with ENE employers requirements. | [14 empty] | Requirement ID - 005 | Accepted |  |  |  | Requirement ID - 005
Requirements for the Manufacture / Installation / Construction
Requirement ID - 006 The ENE D&B Contractor must perform erection of OCS poles | [14 empty] | Requirement ID - 006 | Accepted |  |  |  | Requirement ID - 006
Requirement ID - 007 The ENE D&B Contractor must perform installation of catenary and wires at OCS poles | [14 empty] | Requirement ID - 007 | Accepted |  |  |  | Requirement ID - 007
Integration / Validation / Testing & Commissioning Requirements
Requirement ID - 008 The ENE D&B Contractor must perform inspection of foundation prior to OCS pole installation | [14 empty] | Requirement ID - 008 | Accepted |  |  |  | Requirement ID - 008

## Requirements Earthing
Guideline: Area to be filled in by Interface Expert (RBR or IBs)
REQUIREMENTS SPECIFICATION |  |  |  |  | SOLUTION DETAILS (if any) | [5 empty] | Left: Area for Responsible and Supporting Entities Right: Area for IF Expert (RBR/IB) | AGREEMENT ON REQUIREMENTS' IMPLEMENTATION AND PHASE IN WHICH WILL BE IMPLEMENTED
REQUIREMENTS APPLICABLE TO BOTH ENTITIES |  | Type of requirement | REFERENCE TO PARENT REQUIREMENTS (DESIGN GUIDELINES, ICF, STANDARDS ETC..) |  | Entity proposer of the solution (optional - support columns for the requirements discussion RE-SE) | Solution Proposed (optional - support columns for the requirements discussion RE-SE) | SCOPE SPLIT |  | Implementation Status (Connection OK, Connection NOK, Unknown) | Details of Implementation status (if NOT OK) |  | Interfacing Assets |  | Location [BP, Construction Object, Track Object] | Responsible Entity |  |  |  |  | Supporting Entity
|  | Generic/Specific | Document Number of Generic ICF and/or Design Guideline | Document Revision |  |  | Scope for Responsible Entity | Scope for Supporting Entity |  |  |  | Asset Type / Discipline [Funct.Class name] | Site ID / Connection Point - interfacing assets |  | Requirement ID + source | Status Applicable/Not applicable/ Implemented/Rejected/Accepted but not implemented/Under discussion/ | Phase to be Implemented (if Accepted) | Reasons for Rejection (if Rejected) | Decision/Comments Filled in by RE IF Expert | Requirement ID + source | Status Applicable/Not applicable/ Implemented/Rejected/Accepted but not implemented/Under discussion/ | Phase to be Implemented (if Accepted) | Reasons for Rejection (if Rejected) | Decision/Comments Filled in by RE IF Expert
Requirement ID - 101 The INFRA & FAC DTD Consultants, INFRA & FAC Build Contractor and ENE D&B Contractor shall arrange earthing and bonding for their respective systems in areas of possible future electrification. | [14 empty] | Requirement ID - 101 | Accepted |  |  |  | Requirement ID - 101
Requirement ID - 102 The interfaces between INFRA Build Contractor (responsible for construction of ML INFRA and FAC) and ENE D&B Contractor earthing and bonding shall be arranged and coordinated. | [14 empty] | Requirement ID - 102 | Accepted |  |  |  | Requirement ID - 102
Requirement ID - 103 The general concept of earthing and bonding system shall be according to the Figure 1 below and requirements of RBDG-MAN-020: | [14 empty] | Requirement ID - 103 | Accepted |  |  |  | Requirement ID - 103
Requirement ID - 104 In context of DG RBDG-MAN-020 the maximum allowed touch voltages shall be fulfilled according to EN 50122-1 limits but with some more restrictive value (50V for long term touch voltages in general locations and 25V in workshops). | [14 empty] | Requirement ID - 104 | Accepted |  |  |  | Requirement ID - 104
Requirement ID - 105 EN 50122-1, defines the zones OCLZ (Overhead Contact Line Zone) and CCZ (Current Collector Zone) as the zones not exceeded by a broken overhead contact line or energized dewired or broken current collector, as shown in the Figure. TOR Top of rail HP Highest point of the overhead contact line OCLZ Overhead contact line zone CCZ Current Collector zone TCL Track centre line X Width of the overhead contact line zone: 3.2 m Y Width of the pantograph zone from the centre of the track: 2 m Z SH – HP: 2 m S1 Width of lateral movement of the pantograph S2 Lateral safety distance for the broken or dewired pantograph (design-dependent) S3 Vertical safety distance for the broken pantograph (design-dependent) Sel Electrical clearance (270 mm) SH Maximum height of the CCZ (8m). The value can be slightly lower in on site circumstances, where SH = HP + Z. LP Current collector width HP Maximum height of the fully uplifted current collector. Inside such zones, conductive parts of structures and equipment (accidentally) can receive the contact of live parts, so, as general rule must be connected to return circuit (earthed) to reduce the voltages transferred by means of indirect contact mechanism (EN 50122-1). | [14 empty] | Requirement ID - 105 | Accepted |  |  |  | Requirement ID - 105
Requirement ID - 106 The main procedures and actions to do are: • Connection of the return circuit to the main earthing bar of the facility; • The OCS related equipment will be connected to return circuit as routine part of OCS erection works; • The non-OCS LV equipment (e.g., Information panels, platform lighting…) inside the OCLZ zone shall have an earthing arrangement (protection wire) connected to the main earthing bar of the facility or directly to the return circuit; • All facility structures shall have a structure earth including a foundation earth electrode. The structures shall have been constructed including main earthing bars had been left prepared for connection to the return circuit. The connection will be realized at each prepared connecting point; • All facility metalwork shall be bonded to the facility earth which is in turn bonded to the traction earth (return wire or track) at the main earthing bars; • Other longitudinal infrastructures outside the OCLZ like fences and retaining walls shall be isolated or connected to the return circuit as function of the distances and layout; • Infrastructures entering and leaving the facility like water or gas pipes shall be insulated by means of insulation joints to avoid transferred potentials. After insulation, the pipes can be freely earthed (if needed). | [14 empty] | Requirement ID - 106 | Accepted |  |  |  | Requirement ID - 106
SCOPE SPLIT - REQUIREMENTS APPLICABLE TO ONE ENTITY
Responsible Entity of the Implementation | Supporting Entity of the Implementation
Requirements for the Design | [10 empty] | Left: Area for Responsible and Supporting Entities Right: Area for IF Expert (RBR/IB)
Requirement ID - 107 Based on latest version of IMS design the ENE D&B Contractor must develop detailed earthing design for ENE Equipment, including connections to FAC earthing where applicable and fulfillment of requirements ID 101 to ID 106. | [14 empty] | Requirement ID - 107 | Accepted |  |  |  | Requirement ID - 107
| Requirement ID - 108 The FAC DTD Consultant must provide latest version of IMF design to ENE D&B Contractor. | [13 empty] | Requirement ID - 108 | Not applicable |  |  |  | Requirement ID - 108
Requirements for the Manufacture / Installation / Construction
Requirement ID - 109 Design OCS and location of OCS pole foundations; performs connection of their equipment to connection points of the earthing system provided by INFRA & FAC Build Contractors according to the developed design. | [14 empty] | Requirement ID - 109 | Accepted |  |  |  | Requirement ID - 109
| Requirement ID - 110 The INFRA Build Contractor performs construction of the IMF earthing system according to the developed FAC Design consultant design solutions, including connections to INFRA earthing if applicable. | [13 empty] | Requirement ID - 110 | Not applicable |  |  |  | Requirement ID - 110
Integration / Validation / Testing & Commissioning Requirements
Requirement ID - 111 The ENE D&B Contractor performs testing and verification of earthing and bonding system as whole after installing OCS wires and equipment. | [14 empty] | Requirement ID - 111 | Accepted |  |  |  | Requirement ID - 111
| Requirement ID - 112 The FAC Build Contractor performs testing and measurements of earthing and bonding system of the structures constructed by FAC Build Contractor and connections to INFRA earthing if applicable. | [13 empty] | Requirement ID - 112 | Not applicable |  |  |  | Requirement ID - 112

## Requirements Protective Screens
Guideline: Area to be filled in by Interface Expert (RBR or IBs)
REQUIREMENTS SPECIFICATION |  |  |  |  | SOLUTION DETAILS (if any) | [5 empty] | Left: Area for Responsible and Supporting Entities Right: Area for IF Expert (RBR/IB) | AGREEMENT ON REQUIREMENTS' IMPLEMENTATION AND PHASE IN WHICH WILL BE IMPLEMENTED
REQUIREMENTS APPLICABLE TO BOTH ENTITIES |  | Type of requirement | REFERENCE TO PARENT REQUIREMENTS (DESIGN GUIDELINES, ICF, STANDARDS ETC..) |  | Entity proposer of the solution (optional - support columns for the requirements discussion RE-SE) | Solution Proposed (optional - support columns for the requirements discussion RE-SE) | SCOPE SPLIT |  | Implementation Status (Connection OK, Connection NOK, Unknown) | Details of Implementation status (if NOT OK) |  | Interfacing Assets |  | Location [BP, Construction Object, Track Object] | Responsible Entity |  |  |  |  | Supporting Entity
|  | Generic/Specific | Document Number of Generic ICF and/or Design Guideline | Document Revision |  |  | Scope for Responsible Entity | Scope for Supporting Entity |  |  |  | Asset Type / Discipline [Funct.Class name] | Site ID / Connection Point - interfacing assets |  | Requirement ID + source | Status Applicable/Not applicable/ Implemented/Rejected/Accepted but not implemented/Under discussion/ | Phase to be Implemented (if Accepted) | Reasons for Rejection (if Rejected) | Decision/Comments Filled in by RE IF Expert | Requirement ID + source | Status Applicable/Not applicable/ Implemented/Rejected/Accepted but not implemented/Under discussion/ | Phase to be Implemented (if Accepted) | Reasons for Rejection (if Rejected) | Decision/Comments Filled in by RE IF Expert
Requirement ID - 201 Protection screens shall be installed in areas with possible future electrification at any location where minimum clearances to accessible live parts according to standard EN50122-1 are not respected as stipulated in Design Guideline RBDG-MAN-019-0103 section 4.13. and in Design Guideline RBDG-MAN-017-0106 item 2.1.2. Solutions to be provided in ENE D&B Contractor's DTD. | [14 empty] | Requirement ID - 201 | Accepted |  |  |  | Requirement ID - 201
Requirement ID - 202 The ENE D&B Contractor design shall be coordinated with INFRA & FAC D&B Contractor design to identify such locations, provide space and / or structure for placement of protection screens. | [14 empty] | Requirement ID - 202 | Accepted |  |  |  | Requirement ID - 202
Requirement ID - 203 Installation of protection screens and connection of protection screens to earthing and bonding system in the area of IMF is in scope of ENE D&B Contractor according to his provaided design solutions. | [14 empty] | Requirement ID - 203 | Accepted |  |  |  | Requirement ID - 203
SCOPE SPLIT - REQUIREMENTS APPLICABLE TO ONE ENTITY
Responsible Entity of the Implementation | Supporting Entity of the Implementation
Requirements for the Design | [10 empty] | Left: Area for Responsible and Supporting Entities Right: Area for IF Expert (RBR/IB)
Requirement ID - 204 The ENE D&B Contractor must develop OCS design and indicate locations where minimum clearances to accessible live parts according to standard EN50122-1 are not respected. For said locations ENE designs protection screens. | [14 empty] | Requirement ID - 204 | Accepted |  |  |  | Requirement ID - 204
| Requirement ID - 205 The FAC DTD Consultant must provide latest version of IMF design to ENE D&B Contractor. | [13 empty] | Requirement ID - 205 | Not applicable |  |  |  | Requirement ID - 205
Requirements for the Manufacture / Installation / Construction
Requirement ID - 206 The ENE D&B Contractor must perform construction of OCS according to the developed design and marks locations where minimum clearances to accessible live parts according to standard EN50122-1 are not respected. | [14 empty] | Requirement ID - 206 | Accepted |  |  |  | Requirement ID - 206
Requirement ID - 207 The ENE D&B Contractor must perform installation of protection screens in locations indicated in ENE OCS design and marked during construction. | [14 empty] | Requirement ID - 207 | Accepted |  |  |  | Requirement ID - 207
Integration / Validation / Testing & Commissioning Requirements
Requirement ID - 208 The ENE D&B Contractor must perform site survey and verify installation of protective screens in locations indicated in ENE OCS design. | [14 empty] | Requirement ID - 208 | Accepted |  |  |  | Requirement ID - 208

## Requirements Traction Return
Guideline: Area to be filled in by Interface Expert (RBR or IBs)
REQUIREMENTS SPECIFICATION |  |  |  |  | SOLUTION DETAILS (if any) | [5 empty] | Left: Area for Responsible and Supporting Entities Right: Area for IF Expert (RBR/IB) | AGREEMENT ON REQUIREMENTS' IMPLEMENTATION AND PHASE IN WHICH WILL BE IMPLEMENTED
REQUIREMENTS APPLICABLE TO BOTH ENTITIES |  | Type of requirement | REFERENCE TO PARENT REQUIREMENTS (DESIGN GUIDELINES, ICF, STANDARDS ETC..) |  | Entity proposer of the solution (optional - support columns for the requirements discussion RE-SE) | Solution Proposed (optional - support columns for the requirements discussion RE-SE) | SCOPE SPLIT |  | Implementation Status (Connection OK, Connection NOK, Unknown) | Details of Implementation status (if NOT OK) |  | Interfacing Assets |  | Location [BP, Construction Object, Track Object] | Responsible Entity |  |  |  |  | Supporting Entity
|  | Generic/Specific | Document Number of Generic ICF and/or Design Guideline | Document Revision |  |  | Scope for Responsible Entity | Scope for Supporting Entity |  |  |  | Asset Type / Discipline [Funct.Class name] | Site ID / Connection Point - interfacing assets |  | Requirement ID + source | Status Applicable/Not applicable/ Implemented/Rejected/Accepted but not implemented/Under discussion/ | Phase to be Implemented (if Accepted) | Reasons for Rejection (if Rejected) | Decision/Comments Filled in by RE IF Expert | Requirement ID + source | Status Applicable/Not applicable/ Implemented/Rejected/Accepted but not implemented/Under discussion/ | Phase to be Implemented (if Accepted) | Reasons for Rejection (if Rejected) | Decision/Comments Filled in by RE IF Expert
Requirement ID - 301 Electrical insulation of tracks and turnout between Facility non-electrified tracks and RB RAIL mainline track shall be implemented to prevent flow of traction return current from mainline tracks to facility non-electrified tracks. Electrical insulation of tracks and turnout between IMF track _____and RB RAIL mainline track siding shall be implemented to prevent flow of traction return current from mainline tracks to IMF tracks, please refer to track schematic layout in Figure 1. (to be updated based on IMF track layout). Location of isolation joint between Mainline and IMF shall be agreed between ML INFRA designer and FAC designer. For these puprose separate ICF between ML INFRA and FAC shall be issued. | [14 empty] | Requirement ID - 301 | Accepted |  |  |  | Requirement ID - 301
Requirement ID - 302 Rail Isolated Joint for connection between RBR main track and IMF tracks shall be included in Facility design by FAC DTD Consultant and constructed by FAC Build Contractor. Requirements for Rail Isolated Joint provided below. | [14 empty] | Requirement ID - 302 | Accepted |  |  |  | Requirement ID - 302
1. RAIL ISOLATED JOINT 1.1. DIMENSIONAL Every fabricated/assembled isolated joint shall be checked for vertical and lateral alignment with 1m long straight edge. The tolerances permitted shall be as under: Vertical alignment – Variation at the joint shall be within +1 mm and -0 mm measured at the end of 1 m straight edge placed at the top of rail head. Lateral alignment – Variation at the joint shall not be more than + 0.5 mm measured at the centre of 1 m straight edge placed along the gauge face. 1.2. INSULATION RESISTANCE IN DRY CONDITION Each joint shall be subjected to insulation resistance test in dry condition. A meggering voltage of 100 V DC shall be applied across the joint. The value of the insulation resistance shall not be less than 25 mega ohms. 1.3. INSULATION RESISTANCE TEST IN WET CONDITION The joints shall be immersed in water for 48 hours in suitable clean water tank; and resistance shall be measured immediately after taking out the joint from the water by applying meggering voltage of 100 V DC across the joint and measuring current by an ammeter capable of measuring current up to micro-amperes. The insulation resistance determined by the ratio of voltage to current in amperes shall not be less than 3 kilo-ohms for each of the joint. | [11 empty] | - | - | - | - | - | - | - | - | -
SCOPE SPLIT - REQUIREMENTS APPLICABLE TO ONE ENTITY
Responsible Entity of the Implementation | Supporting Entity of the Implementation
Requirements for the Design | [10 empty] | Left: Area for Responsible and Supporting Entities Right: Area for IF Expert (RBR/IB)
| Requirement ID - 303 FAC DTD Consultant in the design stage must design Rail Isolated Joint for connection between RBR main track and facility non-electrified tracks. Locations of rail isolated joints shall be coordinated with mainline track designer. | [13 empty] | Requirement ID - 303 | Not applicable | - |  |  | Requirement ID - 303
Requirements for the Manufacture / Installation / Construction
| Requirement ID - 304 FAC Build Contractor in the construction stage must install Rail Isolated Joint for connection between RBR main track and facility non-electrified tracks. | [13 empty] | Requirement ID - 304 | Not applicable | - |  |  | Requirement ID - 304
Integration / Validation / Testing & Commissioning Requirements
Requirement ID - 305 ENE D&B Contractor in the T&C stage must verify testing results of FAC Build Contractor and tests that there is no return current leakage to Facility in the location of Rail Isolated Joint. | [14 empty] | Requirement ID - 305 | Accepted |  |  |  | Requirement ID - 305
| Requirement ID - 306 FAC Build Contractor in the T&C stage must test Rail Isolated Joint insulation resistance. | [13 empty] | Requirement ID - 306 | Not applicable | - |  |  | Requirement ID - 306
| Requirement ID - 307 FAC Build Contractor in the T&C stage must make testing protocols available to ENE D&B Contractor. | [13 empty] | Requirement ID - 307 | Not applicable | - |  |  | Requirement ID - 307

## Requirements General
Guideline: Area to be filled in by Interface Expert (RBR or IBs)
REQUIREMENTS SPECIFICATION |  |  |  |  | SOLUTION DETAILS (if any) | [5 empty] | Left: Area for Responsible and Supporting Entities Right: Area for IF Expert (RBR/IB) | AGREEMENT ON REQUIREMENTS' IMPLEMENTATION AND PHASE IN WHICH WILL BE IMPLEMENTED
REQUIREMENTS APPLICABLE TO BOTH ENTITIES |  | Type of requirement | REFERENCE TO PARENT REQUIREMENTS (DESIGN GUIDELINES, ICF, STANDARDS ETC..) |  | Entity proposer of the solution (optional - support columns for the requirements discussion RE-SE) | Solution Proposed (optional - support columns for the requirements discussion RE-SE) | SCOPE SPLIT |  | Implementation Status (Connection OK, Connection NOK, Unknown) | Details of Implementation status (if NOT OK) |  | Interfacing Assets |  | Location [BP, Construction Object, Track Object] | Responsible Entity |  |  |  |  | Supporting Entity
|  | Generic/Specific | Document Number of Generic ICF and/or Design Guideline | Document Revision |  |  | Scope for Responsible Entity | Scope for Supporting Entity |  |  |  | Asset Type / Discipline [Funct.Class name] | Site ID / Connection Point - interfacing assets |  | Requirement ID + source | Status Applicable/Not applicable/ Implemented/Rejected/Accepted but not implemented/Under discussion/ | Phase to be Implemented (if Accepted) | Reasons for Rejection (if Rejected) | Decision/Comments Filled in by RE IF Expert | Requirement ID + source | Status Applicable/Not applicable/ Implemented/Rejected/Accepted but not implemented/Under discussion/ | Phase to be Implemented (if Accepted) | Reasons for Rejection (if Rejected) | Decision/Comments Filled in by RE IF Expert
SCOPE SPLIT - REQUIREMENTS APPLICABLE TO ONE ENTITY
Responsible Entity of the Implementation | Supporting Entity of the Implementation
Requirements for the Design | [10 empty] | Left: Area for Responsible and Supporting Entities Right: Area for IF Expert (RBR/IB)
Requirement ID -601 ENE D&B Contractor shall use the latest available IMF design information (e.g., as-built documentation). | [14 empty] | Requirement ID - 601 | Accepted |  |  |  | Requirement ID - 601
Requirements for the Manufacture / Installation / Construction
Requirement ID -602 ENE D&B Contractor shall fully align its construction activities with ongoing or planned IMF construction works, including adherence to the time schedule, work execution plan, and related documentation. | [14 empty] | Requirement ID - 602 | Accepted |  |  |  | Requirement ID - 602
Integration / Validation / Testing & Commissioning Requirements

## Requirements Traction Power
Guideline: Area to be filled in by Interface Expert (RBR or IBs)
REQUIREMENTS SPECIFICATION |  |  |  |  | SOLUTION DETAILS (if any) | [5 empty] | Left: Area for Responsible and Supporting Entities Right: Area for IF Expert (RBR/IB) | AGREEMENT ON REQUIREMENTS' IMPLEMENTATION AND PHASE IN WHICH WILL BE IMPLEMENTED
REQUIREMENTS APPLICABLE TO BOTH ENTITIES |  | Type of requirement | REFERENCE TO PARENT REQUIREMENTS (DESIGN GUIDELINES, ICF, STANDARDS ETC..) |  | Entity proposer of the solution (optional - support columns for the requirements discussion RE-SE) | Solution Proposed (optional - support columns for the requirements discussion RE-SE) | SCOPE SPLIT |  | Implementation Status (Connection OK, Connection NOK, Unknown) | Details of Implementation status (if NOT OK) |  | Interfacing Assets |  | Location [BP, Construction Object, Track Object] | Responsible Entity |  |  |  |  | Supporting Entity
|  | Generic/Specific | Document Number of Generic ICF and/or Design Guideline | Document Revision |  |  | Scope for Responsible Entity | Scope for Supporting Entity |  |  |  | Asset Type / Discipline [Funct.Class name] | Site ID / Connection Point - interfacing assets |  | Requirement ID + source | Status Applicable/Not applicable/ Implemented/Rejected/Accepted but not implemented/Under discussion/ | Phase to be Implemented (if Accepted) | Reasons for Rejection (if Rejected) | Decision/Comments Filled in by RE IF Expert | Requirement ID + source | Status Applicable/Not applicable/ Implemented/Rejected/Accepted but not implemented/Under discussion/ | Phase to be Implemented (if Accepted) | Reasons for Rejection (if Rejected) | Decision/Comments Filled in by RE IF Expert
Requirement ID - 401 Traction power feeding concept •no traction substations specifically dedicated to feed these facilities is foreseen in ENE Architecture. The traction power is provided through OCS switches from TPS facilities foreseen for the mainline; •if another traction power source is present, it shall be paid attention on the risk of parallel feeding among two different sources (i.e. Need of neutral sections); | [14 empty] | Requirement ID - 401 | Accepted |  |  |  | Requirement ID - 401
SCOPE SPLIT - REQUIREMENTS APPLICABLE TO ONE ENTITY
Responsible Entity of the Implementation | Supporting Entity of the Implementation
Requirements for the Design | [10 empty] | Left: Area for Responsible and Supporting Entities Right: Area for IF Expert (RBR/IB)
Requirements for the Manufacture / Installation / Construction
Integration / Validation / Testing & Commissioning Requirements

## Requirements LandPlot
Guideline: Area to be filled in by Interface Expert (RBR or IBs)
REQUIREMENTS SPECIFICATION |  |  |  |  | SOLUTION DETAILS (if any) | [5 empty] | Left: Area for Responsible and Supporting Entities Right: Area for IF Expert (RBR/IB) | AGREEMENT ON REQUIREMENTS' IMPLEMENTATION AND PHASE IN WHICH WILL BE IMPLEMENTED
REQUIREMENTS APPLICABLE TO BOTH ENTITIES |  | Type of requirement | REFERENCE TO PARENT REQUIREMENTS (DESIGN GUIDELINES, ICF, STANDARDS ETC..) |  | Entity proposer of the solution (optional - support columns for the requirements discussion RE-SE) | Solution Proposed (optional - support columns for the requirements discussion RE-SE) | SCOPE SPLIT |  | Implementation Status (Connection OK, Connection NOK, Unknown) | Details of Implementation status (if NOT OK) |  | Interfacing Assets |  | Location [BP, Construction Object, Track Object] | Responsible Entity |  |  |  |  | Supporting Entity
|  | Generic/Specific | Document Number of Generic ICF and/or Design Guideline | Document Revision |  |  | Scope for Responsible Entity | Scope for Supporting Entity |  |  |  | Asset Type / Discipline [Funct.Class name] | Site ID / Connection Point - interfacing assets |  | Requirement ID + source | Status Applicable/Not applicable/ Implemented/Rejected/Accepted but not implemented/Under discussion/ | Phase to be Implemented (if Accepted) | Reasons for Rejection (if Rejected) | Decision/Comments Filled in by RE IF Expert | Requirement ID + source | Status Applicable/Not applicable/ Implemented/Rejected/Accepted but not implemented/Under discussion/ | Phase to be Implemented (if Accepted) | Reasons for Rejection (if Rejected) | Decision/Comments Filled in by RE IF Expert
Requirement ID - 501 For future electrificaton landplot shall be reserved for ECCS and TPS equipment on site. Necessary land plot dimensions should be indicated (found in IMF design, or additional land acquisition if necessary) by ENE D&B Contractor. | [14 empty] | Requirement ID - 501 | Accepted |  |  |  | Requirement ID - 501
Requirement ID - 502 During the construction phase there shall be possibility to allocate space for storage of ENE equipment and materials. Necessary m2 of space shall be indicated by ENE D&B Contractor. Coordination to be performed between ENE D&B Contractor and Facility Build Contractor. | [14 empty] | Requirement ID - 502 | Accepted |  |  |  | Requirement ID - 502
Requirement ID - 503 During the construction phase there shall be possibility to allocate at least 1 connected to the mainline track for parking of ENE rail vehicles and equipmen. Coordination to be performed between ENE D&B Contractor and Facility Build Contractor. | [14 empty] | Requirement ID - 503 | Accepted |  |  |  | Requirement ID - 503
SCOPE SPLIT - REQUIREMENTS APPLICABLE TO ONE ENTITY
Responsible Entity of the Implementation | Supporting Entity of the Implementation
Requirements for the Design | [10 empty] | Left: Area for Responsible and Supporting Entities Right: Area for IF Expert (RBR/IB)
Requirement ID - 504 ENE D&B Contractor shall define the size of landplot that shall be reserved for future ECCS and TPS equipment on site. | [14 empty] | Requirement ID - 504 |  |  |  |  | Requirement ID - 504
| Requirement ID - 505 FAC DTD Consultant shall ensure in facility layout design reservation of landplot for future ECCS and TPS equipment on site. | [13 empty] | Requirement ID - 505 | Not applicable | - |  |  | Requirement ID - 505
Requirements for the Manufacture / Installation / Construction
Requirement ID - 506 ENE D&B Contractor shall define the requirements for storage and parking areas as per requirements ID 502 and ID 503. | [14 empty] | Requirement ID - 506 |  |  |  |  | Requirement ID - 506
| Requirement ID - 506 ENE D&B Contractor and FAC Build Contractor or Implementing Body shall agree on provaiding to ENE D&B Contractor storage and parking space as per requirements ID 502 and ID 503. | [13 empty] | Requirement ID - 507 | Not applicable | - |  |  | Requirement ID - 507
Integration / Validation / Testing & Commissioning Requirements

## References
References
Ref: | Document Number: | Document Title:
1. | RBGL-DMT-TPL-Z-00021 | Interface Control Form Template
2. | RBDL-DMT-LST-Z-00001 | Product Breakdown Structure (PBS)
3. | RBDG-MAN-017-0106
4. | RBDG-MAN-019-0103
5.
6.