CENTRALISED VOICE COMMUNICATION SYSTEM OF ORO NAVIGACIJA

TECHNICAL SPECIFICATION

Preamble

  - This document contains the technical specification of the Voice Communication System, which the Public limited liability company “Oro navigacija” (hereinafter referred to as “the Customer”) intends to purchase to provide air traffic services in the airspace of Lithuania.

  - Due to the aim of installing the central part of the voice communication system in one place and spreading the operator workstations across all air traffic units of "Oro navigacija", this voice communication system will be called the Centralized Voice Communication System (hereinafter referred to as "System").

System Overview

  - General

    - The System shall be operationally proven, shall have a high availability, shall be fully re-configurable and shall represent state of the art VoIP based technology.

    - The System shall consist of the following segments:

- Air-Ground Communications for voice contact between pilots and air traffic controllers,

- Ground-Ground Communications for voice contact between controllers within the same unit and with other units.

    - The following voice communication facilities shall be available:

- Voice interconnection between internal users,

- Voice interconnection between internal users and external units,

- A/G radio channel selection and operation,

- Monitoring and control facilities,

- Legal voice recording to external voice recorder.

    - The System shall have technically integrated functional parts for telephone and radio connections from operator working positions.

  - System Locations

    - The System cabinet shall be installed in the Customers technical room in Vilnius.

    - The operator working positions (OWP) shall be installed in Kaunas APP/TWR, Palanga APP/TWR, Vilnius APP/TWR/BRF, Vilnius rAPP/rTWR and Vilnius ACC/FIS/FMP/RCC as is specified in Annex 1.

    - The System monitoring and control workstations – technical control terminals (TCT) shall be installed in Kaunas TCS room, Palanga TCS room, Vilnius TCS room and Vilnius System administrator room.

  - Scope of the System

    - The OWPs shall be installed at the following sites of the Customer:

      - Vilnius:

- APP/TWR/BRF – 7 OWPs,

- rAPP/rTWR – 5 OWPs,

- ACC/FIS/FMP/RCC – 18 OWPs,

- TCS room – 1 OWP,

- TPP (Technical test position) – 1 OWP.

      - Kaunas:

- APP/TWR room – 4 OWPs,

- TCS room – 1 OWP.

      - Palanga:

- APP/TWR room – 3 OWPs,

- TCS room – 1 OWP.

    - The names, roles, number, and composition of the OWPs are given in Annex 1.

    - The OWPs shall be suitable for installation on the desktop of controller working position (movable TSS with adjustable tilt housing, sockets for audio devices, mounting of loudspeakers, cabling, etc).

    - Only one OWP – Technical test position (TTP) shall be mounted into cabinet.

    - The desktop OWPs shall be adaptable to the place. TSSs and loudspeakers shall be placed on the desktop of the table and audio devices as well. If OWP has additional parts (communication unit, redundant power supply, etc.) they shall be installed inside console.

    - The box with 3 sockets for audio devices (1 for handset, 1 for headset or hand microphone, and 1 for instructor headset) shall be installed on the bottom of the desktop, which shall be attached firmly.

    - Instructor socket of each position shall override the transmission path of both telephone and radio calls. This is required in order to have full Trainer/Student facilities.

  - Existing Radio Installations

    - The existing VHF Air-Ground communication system of the Customer consists of the local and remote radio sites as is specified in Annex 2.

    - Local and remote radios are VoIP compatible according to EUROCAE ED-137C and are connected to the protected IP network of the Customer.

  - Interoperability, Compatibility and Conformity

    - The System and its subsystems shall meet all associated interoperability requirements according to EUROCAE ED-137C Interoperability Standards for VoIP ATM Components.

    - System shall be compatible to connect the IP based radios via IP network according to EUROCAE ED-137C.

    - The System shall meet with the regulatory material of EASA Detailed Specifications and Acceptable Means of Compliance & Guidance Material for certification or declaration of design compliance of ATM/ANS ground equipment (DS-GE.CER/DEC) and the Supplier shall provide evidence on this.

  - Network architecture

    - The expected possible network architecture is presented in Annex 4.

    - The Supplier shall be responsible for the installation and configuration of the Voice Communication System (VCS) internal LAN on agreed locations.

    - The locations in Vilnius are interconnected by single-mode fiber (SMF) with LC connectors. The Supplier shall ensure that the proposed equipment is capable of interconnecting all Vilnius locations. All provided SFP modules for SMF shall be of BiDi type (utilizing a single fiber strand for bidirectional transmission).

    - Each location shall deploy a minimum of two (2) network switches dedicated to the Voice Communication System connectivity.

    - The switches shall be configured in a redundant pair, ensuring that the failure of a single switch does not result in loss of connectivity (elimination of any single point of failure at the location level). Endpoints shall be dual-homed to both switches.

    - The remote locations in Palanga and Kaunas shall be interconnected via the OTN (Optical Transport Network) provided by ON.

    - The Supplier shall be responsible for the termination of OTN channels into the Voice Communication System internal network, ensuring proper integration and end-to-end connectivity. The provided dedicated throughput per OTN channel shall be 1 Gbps.

    - The OTN network is based on a ring topology. The Supplier’s equipment shall support and utilize this topology to ensure stability, redundancy, and high availability with sub-second failover.

    - The Voice Communication System shall be exposed to external networks only via a Session Border Controller (SBC), deployed in HA. Direct exposure of VCS components to external or untrusted networks shall not be permitted. The SBC shall serve as the security, signaling, and media control boundary for all external interconnections.

System Functional Requirements

  - General

    - This section describes the telephone and radio functionality required at a working position.

    - The System shall support all functions and shall be possible to assign any or all functions to any working position.

    - It is envisaged the “display field” shall be on individual keys or be an area of the HMI where all information is displayed, or a combination of both.

    - The “active call area” shall be a key, or number of keys, where any call other than a DA call, could appear for the purpose of initiating a subsequent function.

  - Ground Telephone Operational Functions

    - Definitions

      - Terminal Busy: the condition that arises when an incoming call has reached the B-party OWP but there is no resource available to present the call to the user. The Terminal busy condition shall not arise on a DA call but is possible for an IA call in the event that the incoming call queue is full.

      - Network Busy: the condition that arises when there is no spare capacity within the network that is providing connectivity between one System and another. This identification may arise as a consequence of either network congestion or (exceptionally) as a result of a command from a System Management Terminal. Throughout these requirements, the term “congestion” is used synonymously with “network busy”.

      - Call Parties: the terms A-party, B-party and C-party are used throughout these specifications to identify the users involved in a telephone call, as follows:

A-party: the user who initiates a telephone call – the calling party,

B-party: the user who first receives the telephone call – the called party,

C-party: any other party involved in an established call.

      - Dynamic Display: a device used for the visual presentation of operational information such as caller identities, call status and programmable touch-keys.

      - Facility: the term “facility” is used to describe the function to be carried out.

      - Feature: the term “feature” gives further details or the particular attributes of the facility.

      - Key: throughout these requirements, the term “key” is to mean a physical button or an appearance on a touchscreen and is used to refer to a single activation device such as a key, switch, button or an icon.

      - Monitor: the audio monitor facility is a means by which it is possible for one controller to be able to listen to the audio/voice activities at the OWP of another controller who is usually not physically adjacent.

      - Normal/Abnormal: the terms “normal” and “abnormal” refer to when the Performance criteria defined for each facility are either met or infringed respectively.

      - Supervisory Tones: the various supervisory tones and announcements shall apply:

- Dial ‒ returned to a user when that user indicates to the System readiness to dial (for example, taking the telephone set off-hook).

- Ringing ‒ returned to the A-party after successful call establishment and prior to call acceptance.

- Terminal busy ‒ returned to the A-party if all available voice paths to a user are occupied.

- Congestion ‒ returned to the A-party if a call cannot be completed to the required B-party due to all appropriate inter-System links being occupied or otherwise unavailable.

- Number Unobtainable ‒ returned to the A-party if a terminal is “Out of Service” or the B-party address is unassigned.

- Interrupt warning ‒ injected into the voice path to warn a party of the imminent priority interruption of an established call.

- Intrusion warning ‒ injected into the voice path to warn a party of the imminent priority conferencing of an established call.

      - User: an Air Traffic Controller or other operational person carrying out the duties of Air Traffic Management.

    - Access methods of telephone facility by which calls can be made:

- Direct Access (DA),

- Instantaneous Access (IA),

- Indirect Access (IDA).

    - Direct Access Calls

      - With this facility the operation of a single key by the A-party is all that is required to initiate a call. The means by which, when accessing a single key, a connection shall be established to a predetermined destination.

      - At least 120 DA keys on each OWP shall be available. DA keys shall be devided to pages or groups, each of them shall contain at lest 40 DA keys.

      - The B-party address is assigned and fixed semi-permanently in the A-party System and is thus uniquely associated with each key and each key is labelled as such.

      - Dial tone and outgoing signalling tones are not given to the A-party.

      - Ringing tone shall be given (and/or visually indicated).

      - Busy tone shall be given if appropriate.

      - “Out-of-service” shall be given should the call fail for any reason other than Busy.

      - The B-party shall be alerted to the presence of the incoming call by audio and or visual means as determined by the B-party System.

      - The A-party identity shall be indicated to the B-party either by association with a key assigned and fixed semi-permanently in the B-party System or by means of a dynamic display.

      - The B-party shall accept the incoming call by means of a single action associated with a key or dynamic display. Due to the exclusive one-to-one assignments of the keys between the A and B-parties or reserved capacity in the B-party dynamic display, it is abnormal for the A-party to encounter the B-party busy; this is a fundamental attribute of the DA Facility.

      - Under normal conditions the B-party can receive one or more DA calls and by observing the identities of the respective A-parties, together with defined operational procedure or (more likely) operational experience, the B-party shall deal with each call appropriately in the appropriate sequence.

      - At the end of a call either the A-party or the B-party shall be able to deselect/clear.

      - DA shall be designed to meet the requirements for Direct Controller-Controller Voice Communication which stipulates that communication be established between radar controllers within 2 seconds in 99% of the time.

      - The delay interval between the A-party initiating the call and the B-party receiving the call alert/indication shall be maximum of 2 seconds.

    - Instantaneous Access Calls

      - IA is a means of “establishing” a telephone communication between two Users where there is an operational requirement for this.

      - With this facility the operation of a single key by the A-party is all that is required to initiate a call.

      - The B-party address is assigned and configured in the A-party System and is thus uniquely associated with a particular key and labelled with the B-party’s identity.

      - Dial tone and out-going signalling tones shall not be given to the A-party. Ringing tone shall not be given to the A-party.

      - “Out-of-Service” tone shall be given to the A-party should the call fail for any reason including any busy conditions encountered.

      - The A-party identity is indicated to the B-party either by association with a key assigned and fixed semi-permanently in the B-party System or by means of a dynamic display. Due to the usually urgent nature of IA calls any visual and/or audible alerts shall be distinctive from other types of call.

      - An audible alert shall be generated at the B-party System in accordance with the following options:

- no audible alert,

- alert of fixed duration.

      - The B-party System automatically accepts the incoming call without any intervention required by the User. This occurs regardless of the B-party being engaged on any other type of call. Thus B-party busy is totally abnormal and should result in “Out-of-Service” tone being given to the A-party. At this stage the speech channel from the A-party to the B-party is established.

      - The B-party may respond to the A-party by activation of a key associated with the incoming call. This action enables the return speech path if it occurs during the current call. Otherwise, it is treated as a new IA call.

      - If the B-party responds during the current call, this has the effect of preventing the call from being cleared until both parties clear the call. Without B-party response, the call is cleared when the A-party terminates the IA call.

      - Call clearing has no effect on other calls in progress at either the A-party or the B-party.

      - IA shall be designed to meet the requirements of Instantaneous Controller-Controller Voice Communication which stipulates that two-way direct communication be established between non-physically adjacent controllers within 1 second or less in 99% of the time.

      - The delay interval between the A-party initiating the call and the A-party to B-party speech path being established shall be maximum of 1 second.

    - Indirect Access Calls

      - The Indirect Access (IDA) facility shall be supported as both Internal and External Facilities using private (PABX) and public (PSTN) telephone services, and VoIP.

      - The IDA facility shall enable A-party to enter a complete B-party address on a telephone dialling keypad to select a network and to cause a call attempt to be made to the supplied address. This is equivalent to normal dialled telephone operation.

      - Ringing tone and busy tone are given to the A-party as appropriate. A suitable mechanism (Out-of-service tone) shall be provided to inform the A-party, should the call fail for any reason other than Busy.

      - It may be possible for calls from more than one A-party to be presented to a B-party simultaneously.

      - It is possible for either the B-party or the A-party to terminate an established IDA call.

      - In addition to dialling the B-party address in full, the following PABX-type facilities are also used to establish IDA calls:

        - Abbreviated Dialling within the phonebook: entering a short code (up to four digits, a character string of unrestricted length or a specific labelled key) on a telephone dialling keypad, shall cause a call attempt to be made from the A-party to a predefined B-party associated with the supplied code.

        - Last Number Redial via call history: operation of a key shall cause a call attempt to be made from the A-party to the B-party to which the most recent previous call attempt (successful or unsuccessful) was made.

      - Phonebook functionality shall be available at all positions to enable the caller to find necessary calling party by name or phone number, or URI.

    - Call Priority

      - The Call Priority facility shall be supported for deployment as both Internal and External Facilities.

      - The call priority facility is a means of attaching an indicator (or flag) to a telephone call to show that it is “urgent” as opposed to “routine”. It is intended for use when it is necessary to make an urgent call concerning the safety of aircraft (i.e., an emergency) and to enable, if necessary, the interruption of less urgent calls in progress at the time. Thus, calls can be made with or without priority so that there are two types as follows:

- priority calls,

- routine calls.

      - The ultimate decision and responsibility as to whether a call is a Priority Call rests with the A-party in accordance with local operational procedures. There are 2 ways in which a priority call can be made:

- manually before the call is first placed: before making the call, operation of a priority key will set the call to “Priority”. This method is used when the call is already known to be urgent,

- automatic setting of priority: calls from either a particular OWP or individual keys are pre-configured “Priority” in the System. This configuration would be established as a contingency for use in special situations only. This type of configuration shall be an easily selectable option by means of the System management terminal.

      - At the OWP receiving a Priority Call the following sequence of events shall take place:

- distinctive and prominent audible and/or visual alerts clearly indicate to the B-party that a priority call has been received,

- the B-party applies discretion as to how the priority call is dealt with, but normally it would be answered as quickly as the prevailing operational circumstances allow.

      - If a priority call cannot proceed due to congestion (all available circuits, links or channels being busy), the priority call shall interrupt an established unprotected routine call (should one exist), thus allowing the priority call to proceed. Before the established routine call is interrupted, all parties engaged in that call shall receive an interrupt warning tone.

    - Call Intrusion

      - The Call Intrusion facility shall be supported. Call Intrusion will be established by bi-lateral agreement but shall be supported for deployment as both Internal and External Facilities.

      - At the OWP receiving a Priority Call, the following sequence of events shall take place:

- The B-party receives, immediately, a pre-defined warning tone, via their telephone equipment, that an intrusion is imminent because of a Priority Call being received. If the call is not accepted this tone may be repeated, periodically, after specified time interval.

- The B-party applies discretion whether to release resources to permit the Priority Call to be answered. The B-party may do this by either clearing a call already in progress or by placing a call on hold.

- If the B-party releases resources, as described above, the Priority Call shall be either answered automatically or presented as a Priority Call as specified by the B-party.

- If the B-party does not release resources within the pre-defined time interval the A-party shall be connected in telephone conference at the OWP, and the warning tone stopped.

      - It shall be possible for any user to be protected against intrusion by other users. This protection shall be selectable either individually on a B-party, user-by-user basis, or as a single parameter for all users connected to a System.

    - Call Interruption

      - The Call Interruption facility shall be supported:

        - In IP networks appropriate measures shall be taken to assure the establishment of priority calls.

        - If the event that Call Interruption does occur in any part of the System all parties engaged in a call to be interrupted shall receive the current indications, by way of an interrupt warning tone before the established routine call is interrupted.

    - Simultaneous Calls

      - A Simultaneous Call occurs when two Users call each other at the same time. Simultaneous calls may arise because of any type of call (IA, DA, and IDA) but the outcome will vary depending upon the specific situation and outcome for both Users shall be a “User Busy” indication.

      - There is specific simultaneous call situation with Users connected to the same System. In this situation, within the performance criteria stipulated for DA and IA calls, a simultaneous call attempt shall result in both Users being connected.

    - Call Queuing

      - The Call Queuing shall be supported to provide a means for a User to have several incoming calls placed in a queue so that the order of their arrival and some means of identifying their origin can be easily determined.

      - Although the means of indicating the order of arrival is implementation specific, it is common for some form of stacking arrangement to be used. Consideration needs to be given to the maximum size of queue that would be considered manageable. Typically, a queue would be 5 or 6 calls deep.

      - The specific Calling Party Identity shall be provided to controllers wherever possible. If it is not possible to provide the specific Calling Party identity, it is recommended that a general identity shall indicate the generic source of the call.

      - The basic attributes of the Call Queuing facility are as follows:

- all calls in the queue are in a calling (ringing) condition until answered,

- a manual process may be used for selecting the next call to be answered but this does not preclude some form of first-in-first-out automatic selection,

- additional indications shall be used to identify Priority Calls that have arrived in the queue. Such indications might include a unique flag against the queue entry, a different display attribute (e.g. flashing characters or a unique colour) and a distinctive audible alert.

      - Although it will usually be IDA calls that are directed to the Call Queuing facility, in some exceptional circumstances (most commonly fault or call diversion conditions) DA calls may also be placed in a call queue. In these cases, some additional means of identifying the call as a DA call shall be given.

    - Outgoing Calls Last Number Redial

      - This function shall enable the user to make a call to the last destination called by accessing a single key within the call history and not redialling the complete number or the abbreviated dialling “code”.

    - End Function

      - It shall be possible to terminate a call by a single key press and by putting the handset on holder (on the base of handset). The holder shall functionally active, the active telephone call shall be terminated when handset is put on holder.

      - Ending a call shall terminate the active call currently in progress and the visual indication shall be extinguished.

    - Supplementary Telephone Services, as described below, shall be supported between ATS units within the Network:

      - The Call Transfer shall enable a user involved in an active call to establish a new call between the other user in the active call and a third party. This function shall enable any call made or received at a working position to be manually redirected to any other party. A Transfer key shall be available, and it shall be possible to transfer any active call at a position to another working position.

      - Call Conference: any OWP shall be able to initiate and manage a Conference. The Conference facility shall enable a minimum of 3 Users and a maximum of 7 Users to speak together. Conferences including external users may be established via external lines of varying types. The System shall support conferences with a maximum of 7 Users, up to 6 of which may be external users connected via external lines. At any stage, any of the Users may leave the conference by de-selecting a key. In such cases the remaining Users shall stay interconnected.

      - Multi Destination Call shall provide direct and immediate communications from a single supervisor position to two or more predefined OWPs. The speech is unidirectional and without a monitoring. Multi Destination Call and their Origin should be indicated at the OWP.

      - Call Hold allows a user to disconnect temporarily from an established call-in order to carry out other telephony functions before returning to the original established call.

      - Call Pickup enables a user to answer a call that is in the alerting phase (ringing) at another user's terminal.

      - Call Diversion enables a user to re-route all incoming telephone and VoIP calls to another user / OWP in the following circumstances:

- if a position is not in use,

- if a busy condition is detected at the B-party,

- if the B-party fails to answer an incoming call within a predetermined time (no reply).

      - Position Monitor: the communications of one user position may be monitored at another user position. Monitoring includes all incoming and outgoing ATS audio.

      - Redial allows the dialling of a previously used destination number again.

  - Radio Functions

    - Definitions

      - User – an Air Traffic Controller or other operational person carrying out the duties of Air Traffic Management.

      - PTT Key – Push to Talk Key – a physical device for carrying out a Push-To-Talk (PTT) action.

      - A/C Call Indication – A/C Call is a term used at the OWP meaning that a transmission is being received on a particular frequency. This event is usually indicated by means of a lamp or other display device.

      - Radio Channel – the term “Radio Channel” is used to specify the frequency in conjunction with a specific radio location when in fact the actual frequency used.

    - Radio Access

      - Radio access at OWP shall be activated by the operation of a key associated with a particular frequency.

      - The key shall enable a particular radio frequency to be in one of four modes:

- Off/Deselected

- Receive only (Rx)

- Transmit and receive (Tx/Rx)

- Cross-coupled

      - A user shall be able to Select or Deselect any Frequency assigned to the working position.

        - Assign a particular frequency:

- there shall be a visual indication that the particular frequency has been assigned to the working position,

- actual frequency shall be displayed in a display field,

- frequency shall be assigned to the working position but shall not be active.

        - Operation of Deselection – re-operate the assigned Frequency key:

- visual indication showing the frequency is assigned at the working position shall be extinguished,

- actual frequency displayed shall be removed from the display field,

- frequency shall no longer be assigned to the working position.

    - Receiving – Frequency Active

      - When “Rx” mode has been selected the User shall hear any transmissions that are made on that frequency. At the same time the presence of the carrier frequency, regardless of speech modulation, shall also cause the A/C call visual indication at the OWP.

    - Audio Device Selection – Rx Mode

      - This facility shall enable the User to select whether transmissions received from aircraft are audible via the hand-held, headset devices and the loudspeaker at the OWP (by adjusting the volume) or to receive transmissions to all these devices simultaneously.

      - The generic audio output for security reasons shall be adjustable via configuration setting only.

      - For safety reasons, the System shall have to ensure that:

- Once the audio device selection for a specific radio channel at a OWP has been completed, this shall be indicated to the user,

- The selection of audio through a headset shall only be allowed if the headset jacks are plugged in the OWP. Compliance with this requirement shall enable the radio channels selected in the headset to be automatically deselected from the headset and selected in the loudspeaker when the jacks are removed. The loudspeaker volume shall be adjustable by the User, but with a limited minimum according to operational requirements; some means of indicating that the loudspeaker volume is at minimum shall be provided. These measures shall guarantee that the audio can be heard at the OWP,

- It shall not be possible to select a frequency without having an audio device (headset or loudspeaker) connected,

- Any frequencies that have been enabled on the System shall not go unmonitored by always ensuring that they are Rx selected on at least one (typically a supervisor’s) OWP,

- Jack-coded plug-in devices (such as headsets) shall be commonly used to determine which (if any) audio devices are connected.

    - Transmitting

      - When both receive and transmit (Tx/Rx) mode has been selected the User shall transmit on the frequency by operating a PTT key. It shall not be possible to transmit on a frequency without receive also being selected.

      - These functions are associated with each frequency and shall enable transmission and reception on an individual frequency. These functions shall only be active once the particular frequency has been selected.

      - Rx selection – an Rx key shall be available and associated with each frequency assigned to the working position.

      - Operation – operate the Rx key associated with the required frequency. There shall be a visual indication that the frequency is in receive mode. All transmissions from aircraft and other working positions transmitting on the particular frequency, shall be received on a loudspeaker or headset/handset at the working position.

      - Re-operate the Rx key – the visual indication showing that the frequency is in receive mode shall be extinguished. Incoming transmissions shall be disconnected from the selected audio device.

      - Tx selection – a Tx key shall be available and associated with each frequency assigned to the working position.

      - Operation – operate the Tx key associated with the required frequency. There shall be a visual indication that the frequency is in transmit mode. A transmitter shall be connected to the frequency.

      - Re-operate the Tx key – the visual indication showing that the frequency is in transmit mode shall be extinguished. The frequency shall be disconnected from the transmitter.

    - Side Tone

      - When transmitting, Side Tone is the User’s own speech fed, at reduced level, into the User’s earpiece in Handset or Headsets. Local generated side tone is recommended to avoid echo triggered by network delays.

    - Multiple Frequencies

      - An OWP shall have radio access to several frequencies, each of which can be set individually in one of the four modes (see 3.3.2.2). Thus, simultaneous reception on more than one frequency is possible. Similarly simultaneous transmission on more than one frequency is possible by operation of a common PTT key.

      - Multi-carrier offset transmission operation function shall be implemented in the System in the ground to air direction by using the off-set carrier, which allows 3 separate radio stations simultaneously transmit the same audio signal using a single frequency assignment, but each using a discrete carrier frequency that is off-set from the assigned frequency.

      - In multi-carrier operation for echo prevention the System shall provide compensation so as to keep time delay differences within the 10ms limit, and the means of compensation shall not in itself result in degradation of voice quality.

    - Transmitter/Receiver Selection

      - The System shall support the following 3 options for Tx/Rx selection:

        - Option 1 – individual transmitter and receiver selection is a System configurable parameter. The User has no means of selection available at the OWP.

        - Option 2 – the User selects at the OWP which transmitter and receiver combinations are in use on each frequency.

        - Option 3 – the User selects at the OWP which transmitter and receiver locations shall be active. Best Signal Selection (BSS) may be used to automatically the specific receiver signal transferred to loudspeaker/headset.

    - Switching Capabilities of Radios

      - In case of failure of any transmitters and/or receivers, the System shall provide the following switching capabilities:

- Automatic switching to alternative transmitters or receivers which could be in different locations to those that have failed.

- Manual switching or Manual switching inhibition of any transmitters or receivers.

      - The System management facility shall provide means by which any round-trip propagation delay may be considered to trigger an alarm. This delay shall be configurable by maintenance personnel.

    - Frequency Cross-Coupling

      - The User shall be able to select two or more radio frequencies in a cross-coupled group.

      - When an aircraft transmits on frequency F1 and is received on the ground, it shall be retransmitted on frequency F2. For the User on the ground at the OWP where coupling has been enabled, when the user transmits on either frequency F1 or F2 transmissions shall occur on both frequencies at the same time.

      - The original aircraft transmission on frequency F1 only shall be fed to the User at the OWP where the cross-coupling has been enabled – not the received signal by retransmission on any other frequencies. The received transmission on frequency F1 is termed the “incoming frequency”.

      - Users shall be given clear indications of which frequencies are being employed in cross-coupled mode.

      - Single coupling group shall be possible per each working position. Of the frequencies in these groups, it shall be impossible to simultaneously assign the same radio frequency to more than one group.

      - To prevent cross-coupling chains, means shall be provided to ensure that a particular frequency can only be included in one cross-coupling session.

      - If a frequency is already cross-coupled on one OWP the System shall prevent it being cross coupled at another OWP – regardless of its location. The System shall also present clear information, on the OWP of the User being prevented from cross coupling the frequency, that the cross-coupling procedure has been refused and thus not executed.

      - The System shall support both duplex and simplex cross-coupling functionality. All received frequencies in duplex mode may be re-transmitted on all the other frequencies in the cross-coupled group - but only one at a time. The received frequency re-transmitted is always presented at the OWP. Received frequencies in simplex mode are never re-transmitted on other frequencies in the cross-coupled group.

    - Status Notification

      - When a User selects a frequency on a OWP terminal in receive mode, the System shall have the capability to make available to the User the following information about the Rx status:

- Confirmation that the Rx is available and ready for use – including the existence or failure of the logical link to the Rx site,

- The identity of the Rx selected.

      - When a User selects a frequency in transmit mode, the System shall have the capability to make available to the User the following information about the Tx status:

- Rx status notification,

- Confirmation that the Tx is available and ready for use – including the existence of a logical link to the Tx site,

- The identity of the Tx selected.

      - In the event of a frequency selection action being rejected, Users shall be informed as to the cause of that rejection. Possible causes for rejection shall include the following:

- The total number of Users with that transmitter selected would exceed the total permissible,

- The transmitter is not available.

      - It is assumed that the unavailability of a logical link (Tx and/or Rx) would be notified in accordance with Rx status notification and Tx status notification and detection of end-to-end connection loss.

    - Frequency Monitoring

      - This function shall enable any working position to monitor all radio traffic on channels that are available at the working position, even if they have been selected at other working positions.

      - Operation:

- select the radio channel to be monitored,

- operate the Rx key associated with that frequency,

- there shall be a visual indication that the frequency is in receive mode.

      - All transmissions from aircraft and working positions shall be received on the selected audio device for that frequency. The above Operations shall be repeated for each frequency to be monitored.

      - To discontinue monitoring a particular frequency:

- re-operate the particular Rx key associated with that frequency,

- visual indication showing that the frequency is in receive mode shall be extinguished,

- all transmissions from aircraft and working positions shall be disconnected from the selected audio device for that frequency.

    - Best Signal Selection

      - Best Signal Selection (BSS) function shall be implemented in the System to handle multi receiver frequencies. This function shall consider the audio signal quality and the relative delay between the incoming signals.

      - It shall be possible for BSS functionality for each frequency (channel) to be manually deselected at the OWP, supervisor position or engineering management system.

      - It shall be possible to deselect one or more individual receivers from BSS at the OWP, supervisor position or engineering management system.

      - If a change of receiver is permitted after original BSS operation, the intelligibility and integrity of the received signal to the controller shall not be degraded.

      - In situations where BSS is used, time delay differences due to the reception of the same signal received from different radio sites shall be compensated for if greater than BSS input delay differential max.

      - In situations where mixed received signals are used in preference to BSS, time delay differences due to the reception of the same signal received from different radio sites may result in echoes at OWP that shall be compensated for if greater than 10 ms. Variation of differential delay shall not affect voice quality of the message received.

      - A selection therefore shall be made to route the best signal of the receivers to the controller. When a message is received on any or all the radios in a BSS group, the System shall evaluate the quality of the signal from each of the receivers in that group. The System shall isolate the signal with the best quality and shall direct only that signal to the selected output audio devices. Any transmissions made from the operator panel on that frequency group, shall be directed to the transmitter site associated with the selected receiver.

      - The operator shall receive a visual indication of the selected radio site.

      - If the operator attempts to transmit on the BSS frequency prior to any message being received on that frequency a default site shall be selected.

      - It shall be possible to override the BSS function from the panel and to select any site of the group.

    - Short-Term Recording

      - The System shall have short-term recording functionality of the last radio and telephone conversations at the OWP level, with a duration of 60 minutes, and with an instant playback function.

      - The playback of the recordings shall be seamless, without interruptions, and the recording shall be identified by icon and additional information (source, channel or number, name, etc.), which shall help user to find easily the necessary recording.

- Note: In the existing VCS longer in duration recordings are broken into parts and playback of these recordings also consists of these parts. In the new System similar situation shall be avoided.

      - It shall be possible to instantly replay the last recording by pressing a dedicated button on TSS.

  - Human Machine Interface

    - General

      - Each User shall interface with the System through an OWP which provides a means of communication for both Ground Telephone and Air-Ground applications.

      - Depending upon the type of ATS functions and tasks to be executed at the positions at the ATS unit, each console shall be provided with the necessary terminal equipment to fulfil the communication requirements.

      - The communication equipment at all positions shall be identical in respect of functions and performance, the quantity in respect of assigned telephone keys or access to frequencies may be different.

      - The terminal equipment, separated into operating panels and control/interface equipment, shall be installed into the ATS working positions (OWP).

    - Activation and Presentation Devices

      - An OWP uses a range of activation and presentation devices to provide access to all of the user-functions implemented by a System.

      - Activation devices:

- Touch-sensitive screens (TSS),

- For the A/G PTT operation shall be mechanical keys, including those that are integrated into hand microphones, handsets, and free or clip-on lapel switches integrated into a headset cable.

      - The ability to re-configure the layout of a User’s System panel is a requirement that prescribes the use of dynamic LCD displays for both activation and presentation with segmented touch-sensitive screens (TSS).

    - Operator Position Panels

      - Each operator position shall have functional panel as required to manage the operational functions of the System for telephone (G/G) and a radio (A/G) communication.

      - The panels shall be of limited size between 11 to 14 inch in diagonal and shall be identical in all positions.

      - All operational functions shall be easily accessed.

      - The function keys shall be of solid, and they shall be designed so that different functions are easily distinguishable.

      - The key size shall be large enough to permit clear texts and shall be in size between 20x20 mm and 30x30 mm.

      - The pressure point shall be distinct and precise and shall give good tactile feedback.

      - All telephone DA, IDA and IC functions shall be integrated into one panel.

      - Each telephone terminal and its DA key allocation shall be agreed in detailed functional specification.

      - Indirect Access (IDA) and Common Control (CC) function shall be part of the panel contains the basic element of the terminal. It shall handle indirect calls and integrate to some extent general control functions like volume control, conference, transfer, hold, etc.

      - All incoming calls for which no DA keys are available at the position shall be routed to the queue for at least to 5 calls.

      - The called position shall be free to choose the sequence of acceptance.

      - The identity of the caller shall be displayed.

      - All missed incoming calls shall be displayed with an identity of the caller.

    - DA/Intercom

      - For each OWP, a certain number of opposite positions (internal or remote) shall exist with which frequent and urgent telephone communications are necessary. To facilitate access to telephone and Intercom, the DA feature shall be required.

      - Each access facility shall consist of an appropriate key with a display containing two lines with at least 5 characters each.

      - The character shall be readable, and its height shall be at least 3 mm.

      - To each access facility a telephone address or an Intercom address shall be attributed.

      - Shall be possible to clearly distinguish between telephone and Intercom.

      - Selection or deselection of an access facility shall be activated by the action of the allocated key.

    - Radio Panel

      - In the operator working positions all radio functions shall be activated via one R/T panel, which shall be integrated to OWP panel.

      - It shall enable access to at least 8 radio channels for transmission and reception by way of loudspeaker or headset, or handset, or to all these devices simultaneously.

      - The radio channels assigned to a working position shall be configurable from any one of the Technical Control Terminals.

      - Reconfiguration of the assigned channels for each position shall also be possible from these control terminals.

      - The frequency allocated to a radio channel shall be indicated with 6 characters plus decimal point (e.g. “123.455”) and the letter “M” that means main or “S” that means standby and any other letter indicates the station symbol.

      - This indication shall be present as soon as, and as long as the frequency is allocated to the particular radio channel.

      - Via an input action on the radio panel by pressing an appropriate key, the allocated radio channel shall be selectable for the monitoring of the reception (Rx mode).

      - Any audio communication on this channel shall be routed to the operators’ headset, or handset or to the loudspeaker according to the operator’s selection or to all these devices simultaneously.

      - This selection of a particular radio channel shall be indicated on the associated position and all other positions with access to the same radio channel as well.

      - The presence of a received A/G communication shall be indicated visually as squelch indication.

    - Transmitter Activation (Traffic Mode)

      - This function enables access to the transmitter. The push-to-talk shall be authorised for the radio channel. Before transmitting on a radio channel, this has to be selected in “Traffic Mode”.

      - When radio channels, more than one, are selected in “Traffic Mode”, the operator shall be able to transmit at the same time on all these channels by only pressing the PTT switch.

      - While the operator is pressing the PTT switch, the status of operating radio channels shall not be allowed to be modified. It shall be allowed to deselect a radio channel while PTT is active.

      - Transmitter activation shall only be possible if a headset or hand microphone or handset is connected to the working position.

    - Touch Sensitive Screen

      - The operator position shall be equipped with a touch-sensitive screen (TSS), where DA, IDA, IC, R/T, and CC facilities shall be implemented.

      - The TSS shall have adjustable tilt to give the operator possibility to change viewing angle for better view of the TSS.

      - The panel shall be adaptable to the operational requirements and each operator action on the input device shall produce a visual change to indicate that it has been considered.

      - This panel shall give a clear indication of all the facilities selected by the operator and the status of channels and/or lines, i.e. “busy state”, “transmit in progress”, “receive state”, etc.

      - As this panel will cover a number of configuration facilities, the “default” screen shall display the basic configuration that is expected to be most frequently used during normal operation.

      - The address of the caller shall be indicated to the called party.

      - A brightness control shall be provided for the TSS in order that the operator can adjust the visual indications according to the environmental lighting.

      - The panel shall contain a volume control for independent volume adjustment for the connected audio devices.

      - In any case, the minimum volume obtainable shall be clearly different from zero.

    - Audible Indication

      - All incoming calls shall be announced by means of a continuous tone. For this purpose, each terminal shall be equipped with a buzzer.

      - It shall be possible to make adjustments of the level. In addition, it shall be possible to switch off the continuous tone by a simple key Operation, but a visual indication of “buzzer off” is necessary.

      - Any further incoming calls shall activate the buzzer for a time of approximately 1.0 second.

      - It shall be possible to have a differentiation in tone for different classes of communications at OWP.

    - Audible Tones at Working Positions

      - Ring-Back Tone

        - After establishing a connection and prior to the acceptance of the call by the called terminal, a ring-back tone shall be sent to the calling user. To check that the connection to the called System is already established and to minimise the acceptance delay, the ring-back shall be sent from the called System.

        - The ring-back tone shall consist of a sequence in which the tone period is shorter than the silent period.

      - Interrupt Warning Tone

        - If an established call is subject to a priority interruption, the parties concerned shall be warned of the imminent interruption.

        - For this purpose, an interrupt warning tone shall be generated and heard for some seconds.

      - Terminal Busy Tone

        - If a terminal is busy, the line to the calling exchange shall be released and the calling terminal shall receive from its own System a busy tone indicating that the System will automatically initiate a repetition of the call.

        - The busy tone shall be a rapid sequence of the same tone in which the duration of the tone is theoretically equal to that of the silence between tones.

      - Unserviceable Tone

        - If a terminal is out of service, not available or if the number dialled has not been allocated, a special tone shall be heard by the calling terminal. The line shall be released, and the calling exchange shall provide the appropriate tone.

    - Audio Devices

      - The audio devices of OWPs are specified in the respective table of the Annex 1 and shall be as following:

- Headsets,

- Hand-held microphones,

- Hand Microphone Telephones (Handsets),

- Loudspeakers.

    - Management of Mixed A/G Radio and Ground Telephone Communications

      - In OWPs if headsets will be used, incoming Ground Telephone calls shall be routed to earpiece.

      - While a Ground Telephone call is in progress Ground Telephone speech a parallel A/G Radio call shall be presented in addition. When the controller replies by activation of his PTT key, the pilot shall receive the transmission in the usual way and Telephone shall be muted.

      - Ground telephone calls shall never be mixed inadvertently with A/G Radio transmissions to the pilot.

    - Audio Devices Common Modules

      - Common modules shall be available for the connection of headsets, handsets, hand microphones and loudspeakers as well as for the control of these audio devices.

      - Headsets, handsets and hand-held microphones shall be supplied with identical plugs for connection to the audio jacks and shall be interchangeable.

      - Radio and telephone communications shall be operated via headsets, handsets, hand-held microphones and loudspeakers.

      - Radio and telephone communications shall be available to receive to all connected audio devices at the position simultaneously or to selected audio devices by the user.

    - Headsets

      - Monoaural headsets will be used for R/T and telephone communications.

      - The monoaural headset shall have single earphone and noise-cancelling microphone. It shall be provided with a coiled cable, equipped with a PTT switch and a clip for fixing it to the operator’s jacket. The clip shall be strong enough to carry the full cable weight and PTT switch.

      - Headset shall be made to use either with left ear or with right ear and microphone position shall be adjustable.

      - The length of the cable, if spread, shall be between 1,5 and 2,5 meters measured from the fixing clip to the connecting plug.

      - The PTT switch shall be mounted near the fixing clip. Between clip and headset straight cabling will be used.

      - Headset samples shall be provided for selection.

    - Handset

      - The Bidder shall propose handsets, which are professional of high quality, lightweight, robust enough and shall be of high degree of reliability.

      - Handsets shall be supplied with rest pad or holder. Holder shall functionally active, the active telephone call shall be terminated when handset is put on holder.

      - Microphone shall be noise cancelling to prevent mutual influences between controllers. The handset shall be provided with a PTT switch, which operates the microphone with radio transmission.

      - The handset shall be provided with a coiled cable 1,5 meters length, if spread. The cable shall be terminated with the same connecting plug as for the headsets.

      - Handsets samples shall be provided for selection.

    - Hand-held Microphone

      - The hand-held microphone shall be equipped with a PTT switch. Microphone shall be noise cancelling to prevent mutual influences between controllers. The cable shall be same length as for the handsets and shall be terminated with the same connecting plug as for the handsets.

      - Hand-held microphones samples shall be provided for selection. Hand-held microphones shall be supplied with either hook or holder or rest pad to put when idle.

    - Loudspeaker

      - Each OWP shall have 2 loudspeaker panels with adjustable audio output.

      - Volume control at the OWP shall be easy reachable and shall be operated electronically or mechanically.

      - With the volume in minimum position, the audio level shall remain sufficient for monitoring purpose.

      - Loudspeaker panels shall be a box type, suitable for desktop and console rail mounting.

      - Loudspeakers shall be connected directly to the sockets with locking mechanism of common modules of audio devices.

      - The loudspeakers shall be connected directly to the common modules of the audio devices with a locking mechanism.

      - Loudspeakers shall be supplied with desktop or rail fixing accessories which shall be agreed with the Customer.

    - Connection of Headsets, Hand microphones and Handsets

      - The headsets, hand-held microphones, and handsets shall be plugged into sockets which shall be installed at the operating consoles of each OWP. The sockets shall be installed in a small box and shall be mounted at the bottom side of the desktop on the left of the operating positions.

      - The plugs connected into the sockets shall not protrude outside the front side of the table shelf. Installation places of the connector boxes may vary from position to position and shall be agreed with the Customer.

      - The sockets can be used in an interchangeable way between audio devices.

      - The plugs shall easily be connected into the sockets and disconnected by the user, but the connector shall fix in the connected position so that it does not easily disconnect. A locking mechanism to prevent plug from disconnection is not required.

    - Monitoring

      - A means of monitoring shall be provided to enable a suitably authorised user to listen in on voice communication from one or more other user terminals.

    - Human Engineering Requirements

      - The following specifications identifies some important human engineering aspects that shall be considered for Human Machine Interfaces (HMI):

      - The interaction between a controller and the HMI shall leave the controller in no doubt about the next action to be taken in implementing the current function.

      - An HMI shall make it clear to the controller what type of input is required at any particular instant.

      - An HMI shall immediately make it clear to the controller that invalid data has been entered.

      - Any message, instruction or information shall be displayed for a sufficient period to allow the controller to read it.

      - Display attributes such as colours, bolding, flashing and highlighting shall only be used in those situations where the impact they cause is essential. Over-use can be distracting and can lead to important messages being ignored.

      - The status of all function keys and DA keys shall always be obvious.

      - Any change in the status of a function key or DA key shall be highlighted by an appropriate means.

      - The availability of a particular function or service shall be shown by the status of the indicator associated with the key that activates the service.

      - The indicator associated with a DA key, or an Instantaneous Access key shall use different attributes (for example, lit, unlit, coloured and flashing) to distinguish between:

- An active call-in progress,

- No active call or service in progress (idle),

- Priority calls,

- Busy/congestion.

      - The indicator associated with the A/C call shall be distinctive to enable active frequencies to be easily identified.

      - A distinctive and clear indicator showing any frequencies that have been cross coupled shall be provided.

      - A set of keys grouped to represent a standard telephone dial-pad shall be available for the entry of numeric (address) data.

      - The displays/indicators shall have:

- Wide viewing angle,

- Adjustable Brightness (day, night, sun glance operation etc),

- Low light reflections obscuring visibility,

- Adjustable tone volume.

    - Physical Environmental Considerations

      - The keys, panels and displays associated with a System are usually located in a combined Work Position that houses the HMI of many other systems comprising the OWP. Care should be taken to ensure that the various components can co-exist in the physical environment intended and that the environment itself is suitable.

      - Particular consideration shall be given to addressing the following known problems:

        - Electrical interference from adjacent units,

        - Inadequate ventilation and excessive heat generation, the latter of which may demand air conditioning for components that would otherwise not need it,

        - Noise generation by cooling or storage devices shall be avoided, thus no fan or mechanical disk drives shall be used for System operator position equipment,

        - All touchable equipment (keys, switches, touch sensor devices etc.) shall be of such kind that it doesn’t feel cold or hot.

  - System Management

    - General

      - A System shall be connected to terminal devices which can be used for System management tasks. The Management Functions have been classified into Management Functional Areas (as per ISO’s OSI Management or equivalent):

- Performance management,

- Fault (or maintenance) management,

- Configuration management,

- Security management.

    - Performance Management

      - Performance management provides functions to evaluate and report upon the behaviour of telecommunication equipment and on the effectiveness of the external links, network or System. Its role is to gather statistical data for the purpose of monitoring and correcting the behaviour and effectiveness of these and to aid in the planning and analysis phases.

      - Performance management relates to the following set of functions:

        - Performance monitoring: the collection of data concerning the performance of the System.

        - Traffic Measurement: the collection of traffic data statistics from System. Traffic data reports may be sent upon threshold triggering, periodically or on demand.

        - Status Monitoring Functions:

- Service availability of the System,

- Status of controls,

- Line busy/idle status,

- Control Functions,

- Quality of service (QoS) observations.

    - Fault Management

      - Fault management functions enable the detection, isolation and correction of abnormal operation of the telecommunication network and its environment.

      - Fault management relates to the following set of functions:

        - Alarm Surveillance: the capability to monitor failures in near real time. When a failure occurs, fault management determines the nature and severity of the fault and may also determine the effect of the fault on the services supported by the faulty equipment.

        - Fault Location: the ability to augment the initial failure information by use of additional failure localization routines.

    - Configuration Management

        - The System shall be configured in accordance with recognized cybersecurity best practices. Configuration shall follow CIS Benchmarks, Security Technical Implementation Guides (STIGs) or other relevant industry standards. The Supplier shall provide configuration compliance documentation; explain any deviations from recommended guidelines, if applicable; ensure that the security configuration is applied prior to system commissioning and maintain the ability to review, update, revert to previous versions and audit the configuration state.

        - The Supplier shall provide a complete list of all software components used within the system (Software Bill of Materials (SBOM) in a selected standardised format. The SBOM must include all software components used in the system, including third-party and open-source software. For each open-source component, the Supplier shall specify the license type and provide assurance that the use of such components does not violate security or licensing requirements.

        - The System shall support only necessary software services and components, allowing execution only of approved (white-listed) programs. All non-essential components (not required for system functionality) shall be disabled prior to system commissioning.

        - The System shall use mechanisms ensuring centralised configuration management, application and verification.

        - Only authorised personnel may initiate hardware or software changes, and all access events shall be logged.

      - Configuration management provides functions to exercise control over, identify, collect data from and provide data to a System and procedures that are necessary to bring equipment into service.

      - Configuration management relates to the following set of functions:

        - Re-configuration: procedures that are necessary to adapt User-facilities like frequencies, DA-key etc. to the actual traffic situation. With particular regard to “user configuration management”, a common requirement is to be able to build and store a particular combination of ground telephone and radio frequency assignments in accordance with a particular operational “role”. Roles may be assigned to a particular OWP by the System Management Terminal or invoked by the User.

        - Status and control: the capability to monitor and control certain aspects of the System on demand. Examples include checking or changing the service state of System sub-parts (in service, out of service, stand-by) and initiating diagnostics tests. When associated with failure conditions, these functions are corrective. Status and control functions can also be part of routine maintenance when execute automatically or on a scheduled periodic basis.

        - Installation: the extension or reduction of System hardware and software components. An important aspect of this function is the ability to make modifications to the configuration while the System continues to operate.

      - Configuration of Telephone and Radio Access Keys

        - Configuration management shall permit the multiple assignment of an access key appearance on more than one OWP.

      - Alpha-numeric Identification Labels

        - To facilitate the presentation of a caller’s identity as an alpha-numeric string (e.g., caller’s name or operational identifier) rather than simply digits representing the caller’s AGVN number, it shall be possible to associate an external number with an alpha-numeric string which can be substituted when a call arrives from that source.

      - Recovery after System Failure

        - On recovery from loss of power to a System or any other fault causing an interruption to service, the System shall be returned to the configuration established prior to the failure or, if this is not possible, to a predefined configuration.

      - In case of malfunctions TSS screen calibration facility shall be implemented.

    - Security Management

      - Compliance with Legislation

        - The Supplier shall comply with the requirements set out in Directive (EU) 2022/2555 of the European Parliament and of the Council of 14 December 2022 for measures to ensure a high common level of cybersecurity across the Union, amending Regulation (EU) No 910/2014 and Directive (EU) 2018/1972 and repealing Directive (EU) 2016/1148 (NIS2 Directive), to the extent applicable under the Supplier’s jurisdiction and legal status. The Supplier shall provide documents confirming compliance with NIS2 and the implementation of a cybersecurity risk management framework.

        - The Supplier shall comply with Commission Delegated Regulation (EU) 2022/1645 of 14 July 2022 laying down rules for the application of Regulation (EU) 2018/1139 of the European Parliament and of the Council, as regards requirements for the management of information security risks with a potential impact on aviation safety for organisations covered by Commission Regulations (EU) No 748/2012 and (EU) No 139/2014 and amending Commission Regulations (EU) No 748/2012 and (EU) No 139/2014 and provide documented evidence of the implemented information security risk management framework when required by the contracting authority or competent authorities.

        - The Supplier shall grant both the Customer or competent authority the right to conduct audits to assess compliance with contractual and applicable regulatory requirements. The Supplier shall fully cooperate during audits, inspections or incident investigations initiated by supervisory bodies under the NIS2 Directive and/or Part-IS regulatory framework. The Supplier shall promptly and without undue delay or obstruction provide all required documentation, records, explanations, and evidence relevant to such audits.

        - The Supplier shall guarantee that the delivered Voice Communication System, including all hardware, software, and licenses, will be fully supported for a minimum of 120 month after the date of system acceptance.

        - If a proprietary (appliance-based) operating system (OS) is used, the Supplier shall provide a formal declaration confirming that the OS will remain under full vendor support during 120 month period, including:

- 	Security patching,

- 	Vulnerability handling, and

- 	Regular maintenance updates.

        - Should the operating system approach end-of-life (EoL) during the 5-year support period, the Supplier shall provide an upgrade or migration path that:

- Does not require full system re-certification, and

- Is delivered at no additional cost to the Purchaser.

        - The Supplier shall provide confirmation that it will not rely on manufacturers, equipment, software maintenance or individuals located in countries or territories deemed untrustworthy under the laws of the Republic of Lithuania:

- Russian Federation,

- Republic of Belarus,

- People’s Republic of China (excluding the Separate Customs Territory of Taiwan, Penghu, Kinmen and Matsu),

- Crimea annexed by the Russian Federation,

- Transnistria not controlled by the Government of Moldova,

- Abkhazia and South Ossetia not controlled by the Government of Georgia (Sakartvelo).

      - Integrity Requirements

        - Data stored in the System shall be protected against unauthorised access, use, modification, disclosure, destruction or loss.

        - The System shall use cryptographic mechanisms to prevent unauthorised disclosure and modification of data, where applicable.

        - The System shall automatically send an alert when integrity violations are detected.

        - The System shall perform integrity verification of all software and firmware components during start-up, restart, shutdown or abort procedures to ensure they have not been modified or corrupted.

      - User Identification and Authentication

        - The System shall use centrally managed user accounts and authentication mechanisms.

        - Access levels shall be implemented based on user roles, and each system user role must be clearly documented.

        - Users shall not be granted administrator privileges. The System shall prevent users from performing actions beyond their assigned privilege level.

        - Administrator functions shall be performed using a dedicated account that is not used for daily user functions.

        - The System shall use only individual user accounts. Logging in using non-personal (shared) accounts (e.g., root, admin) shall not be allowed.

        - The Administrator must authenticate using a unique administrator username and password and, where possible, an additional authentication method.

        - Password requirements for system administration and monitoring workstations shall include:

passwords must consist of uppercase and lowercase letters, numbers and/or special characters, with a minimum length of 15 characters (for administrators accounts).

the System shall require password changes at least every 6 months.

the System shall allow only temporary (initial) passwords for first login with mandatory immediate change to a permanent password. Temporary or initial passwords shall be randomly generated and unique for each user.

The system shall store and transmit passwords only in cryptographically protected. Temporary passwords may be transmitted in plain text but only separately from the username.

        - Password change requirements:

users shall have the ability to change their passwords at any time.

forgotten passwords must be changed and not reused.

The system shall prohibit password reuse: users must not be allowed to use any of their previous 8 passwords.

Password change policies shall not interfere with the operation of the operating system.

        - The system must hide the feedback of authentication information during authentication to protect it from possible unauthorized use. Default manufacturer-set passwords shall not be used in hardware or software components; they must be replaced with passwords that meet the defined security requirements.

        - Passwords shall not be stored in application source code under any circumstances.

        - A maximum of 5 consecutive failed login attempts shall be allowed for users (administrators and system monitoring personnel), after which the account shall be locked.

        - The System shall:

(a) allow authenticated user (administrator) to terminate their communication session by activating a password protected screen lock.

(b) display a clear message confirming that the session has been securely terminated.

        - The System shall not contain any unauthorized or undocumented remote or local access accounts, nor any undocumented functions that could compromise system security.

        - The System shall support mutual cryptographically based authentication of remote applications and users prior to establishing remote connections.

        - If necessary (e.g., for troubleshooting or updates), temporary remote access may be granted to Supplier-designated personnel (as specified in procurement documents). Such access shall be limited to the specific task, provided via a secure VPN solution, and subject to logging, auditing, and activity monitoring.

        - The System shall use static (fixed) address assignment. Each system device must have a permanent, non-changing IP address to ensure operational stability, security and traceability.

      - Audit Log Management Requirements

        - The system shall implement an audit log management component that:

- Collects and stores system operation and usage data;

- Enables audit log analysis, including search and filtering by various parameters;

- Protects log entries from unauthorized or accidental modification;

- Archives audit logs in accordance with defined retention policies;

- Supports the export of selected audit logs to the Customer’s centralized event management system (SIEM). If SIEM integration is not implemented, all audit files must be backed up on separate physical devices or components.

        - The system shall record the following events:

- User login and logout attempts (successful and unsuccessful);

- Actions performed by privileged accounts (e.g., account creation, rights changes, configuration modifications);

- Events related to operating system processes or services;

- Data creation, modification, and deletion;

- Activation, deactivation, or rebooting of system components;

- Authentication events of system and devices;

- Creation, viewing, and deletion of log entries;

- Enabling and disabling of the log collection function.

        - Each log entry shall include at minimum:

- User identifier (including device identification related to the event);

- Event date and precise timestamp (synchronized with a trusted time source);

- Action performed;

- Result (success/unsuccessful);

- Event description.

        - The system shall ensure the integrity and confidentiality of audit data:

          - Events recorded in the System shall be stored in hardware or software components designed for storing audit data;

          - Audit data shall be stored preserving all meaningful aspects of its content;

          - Audit logs shall be protected against modification, deletion, or destruction;

          - Access to audit information shall be restricted to privileged users only;

          - Usage of audit logs shall be monitored and recorded.

        - The system shall support real-time incident detection and generate automatic alerts upon identification of unauthorized or prohibited actions (e.g., signs of intrusion or malware, unusual or unauthorized activity, attempts to bypass security controls, detection of unauthorized hardware or software components).

        - Audit logs shall be retained for no less than 90 calendar days (unless they are exported to the Customer’s SIEM). Older entries shall be automatically deleted. It is strictly prohibited to delete or modify audit data before the retention period expires.

        - In the event of disruptions that prevent audit data from being recorded, the system shall immediately issue an automatic alert.

      - Secure Software Development and Vulnerability Management Requirements

        - The Supplier shall adhere to and provide evidence of compliance with recognized secure software development methodologies, such as ISO/IEC 27034-1 or equivalent frameworks, ensuring the integration of security controls throughout the entire software development lifecycle. The Supplier’s project manager shall ensure that all personnel involved in software development are familiar with these methodologies and apply them in practice.

        - The Supplier, including any subcontractors involved in the delivery, shall disclose all known system vulnerabilities and/or weaknesses and ensure their remediation throughout the system’s lifecycle.

        - The Supplier shall guarantee that the System contains no hidden features that compromise security, including but not limited to malicious software, unauthorized access mechanisms or functions, and other security violations.

        - The System shall incorporate malware protection mechanisms capable of detecting and identifying malicious code and ensuring resilience against its impact.

        - The System shall implement safeguards to protect memory from unauthorized code execution.

        - The Supplier shall provide all necessary conditions for the Customer or an independent third party selected by the Supplier to perform vulnerability scanning of the System. This scanning shall be conducted during the Factory Acceptance Test (FAT), repeated during the Site Acceptance Test (SAT), and performed after each system is updated or upgraded. The Supplier shall not impose any limitations on the scope or frequency of vulnerability scanning.

        - The Supplier shall not implement any measures that interfere with or conceal vulnerabilities to prevent their detection during vulnerability scanning or penetration testing.

        - This activity may be carried out by the Customer’s personnel or by an independent third party selected by the Supplier. If a third party is selected, the following requirements must be met:

- The selected third party must be approved by the Customer, as vulnerability testing may expose sensitive information;

- The third party must be established in an EU or NATO member state;

- The third party must be independent of the manufacturer and free from any conflict of interest;

- The third party must not be involved in the design, development, or deployment of the system under test;

- Vulnerability severity assessment shall be conducted using a recognized evaluation framework, such as CVSS v3.1.

        - In case vulnerabilities are identified, their severity (e.g., critical, high, medium, low, none) and associated risk shall be assessed. The severity and risk levels shall be determined by exclusively  Customer or an independent third party (if they conduct vulnerability assessment). The structured report clearly describing the identified vulnerabilities, their severity, and recommended remediation actions is provided to the Supplier. The Supplier shall remediate all identified vulnerabilities at its own expense. The system may only be deployed in the operational environment once all critical and high-severity vulnerabilities have been resolved, and any remaining medium or low-severity vulnerabilities do not pose an unacceptable risk to system security, reliability, or performance.

        - If the system is accessible via the internet, vulnerability assessments may be conducted more frequently or as needed.

        - All information obtained during the vulnerability management process shall be treated as confidential and may not be disclosed to third parties without prior written authorization from the Customer.

        - During the Factory Acceptance Test (FAT), vulnerability scanning and/or penetration testing shall be performed, and an official remediation plan shall be submitted covering all identified vulnerabilities. The plan must clearly define timelines and responsibilities, and it must be approved by Customer.

        - During the Site Acceptance Test (SAT):

- A repeat assessment shall be conducted using vulnerability scanning and/or penetration testing. No unresolved critical or high-severity vulnerabilities, as determined by Customer or an independent third party, shall remain. The Supplier must submit an official written statement confirming that all critical and high-severity vulnerabilities have been resolved.

- All identified medium or low-severity vulnerabilities must not pose an unacceptable risk to system security, reliability, or performance. The Supplier shall submit a remediation plan with agreed timelines. System Patching and Updates

        - During the system development phase, the Supplier shall use the latest stable versions of software and associated patches. At the stage of system deployment into the operational environment, it must be ensured that the system utilizes the most recent stable software versions, provided this does not alter the fundamental principles of system architecture or functionality. Software components that are in testing stages or officially declared by the software manufacturer as end-of-life—i.e., no longer supported, maintained, or developed—shall not be used.

        - Throughout the system’s lifecycle, updates recommended by the software vendor and operating system providers must be implemented.

        - All software updates shall be thoroughly tested prior to deployment to ensure they do not introduce errors or compatibility issues with other system components or integrated applications.

      - Media Usage (if applicable)

        - All data interfaces (e.g., USB ports) within the system shall be either disabled, mechanically locked, or otherwise blocked to prevent unauthorized access.

        - The use of removable media (USB drives, external hard drives, etc.) shall be restricted and controlled. Removable media shall be scanned for malware before connection to the System.

        - The system shall implement cryptographic mechanisms to ensure the confidentiality and integrity of information stored on digital media (e.g., USB drives, external disks, server SSDs/HDDs, backup storage).

      - Business Continuity and Data Protection

          - The Supplier shall provide a documented description of typical system failures and unforeseen scenarios, including their impact, detection methods, and proposed resolution measures. The document shall include:

- Classification of failures (e.g., software errors, hardware malfunctions, network disruptions, security incidents);

- Indicators and detection mechanisms (e.g., audit log analysis, alerting systems, automated tests);

- Recommended actions for each failure type (e.g., recovery steps);

- Preventive measures to reduce the likelihood of failures;

- Response time and service recovery objectives (if applicable under the SLA);

- Examples scenarios describing system behaviour during unforeseen events (e.g., power outage, DDoS attack).

          - The Supplier shall provide the Customer with a copy of the system’s operating system and software that enables full system recovery in the event of a critical failure. The provided copy must be fully functional, compatible with the existing infrastructure, and capable of launching the system in an alternative environment if the primary infrastructure becomes unavailable.

    - Control Terminals

      - The System shall be supplied with 4 technical control terminals (TCT) for technical and operational control.

      - The connection between the System and each TCT shall be IP based.

      - The TCT shall be based on workstation with a SSD, display, keyboard, mouse, and USB. The diagonal of the display shall be 24 inches to be sufficient for convenient configuration, management and control of the System.

      - Several degrees of access of TCT shall be implement with purpose to allocate different access rights – administrator, supervisor and monitor. This priority shall be allocated by way of software.

      - System administrator shall be responsible to allocate TCT user access rights.

      - TCT shall be installed:

- in the System administrator room in main building of Oro navigacija in Vilnius,

- in the System supervisor room in main building of Oro navigacija in Vilnius,

- in the technical supervisor room in Kaunas site,

- in the technical supervisor room in Palanga site.

    - System On-line Reconfiguration

      - Sometimes one or more elements of an ATC OWP may be “out of service” due to maintenance or technical problems. Such problems must be solved without any disruption to air traffic control by transferring operation to another unused ATC OWP. Such circumstances can be managed by an on-line reconfiguration feature and the dynamic labelling address information.

      - On-line Reconfiguration within a centre shall not have technical or operational impact on adjacent centres.

      - On-line Reconfiguration within a centre shall not have impact on calls that are already established.

      - Incoming and outgoing telephone calls, being established during an on-line reconfiguration, shall be routed to either the original destination or the new destination (after reconfiguration).

      - Any action of the supervisor shall be executed without influence on the normal system operation, existing connections shall not be disturbed, and new connections shall not be delayed.

      - Off-line Reconfiguration

        - Whenever an off-line reconfiguration is required, the downtime of the System shall be kept to a strict minimum, some seconds can be accepted.

      - User’s Reconfiguration

        - The System shall have the ability for a quick, on-line reconfiguration of the ATC sectors, to meet changing demands according to the time of day and the air traffic pattern.

        - For this purpose, up to three different configurations shall be pre-programmed in the System which can be called up by the OCT.

      - Restart

        - All user specified data, which are entered into the System via the control terminal, and which represent the actual status of the System, shall be stored in non-volatile and protected memory space.

        - In case of a System breakdown, it shall be possible to restart the System by means of a “reset”.

        - The System restart time shall be as short as possible via “menu” techniques from one of the control terminals.

        - After a power break, an automatic reset shall occur without loss of data, and the status shall not be affected.

    - Monitoring and Control of the System

      - The correct functioning of the System requirement shall be performed by:

- Efficient self-checking capabilities,

- Periodical failure check procedure of all units not continuously in operation,

- Starting of fault diagnostic programs in case of failure detection,

- Functional unit reconfiguration to enable fail-safe degradation of System operation,

- Indication of failure messages and saving.

      - Fault Indication

        - The System shall run continuous diagnostic checks on the System’s operation and, if a malfunction is detected, it shall raise an alarm. This alarm shall be displayed on the TCT and OCT.

        - The failure message shall contain:

- Time (delay, hour, minutes) of failures,

- Type of failure,

- Equipment involved,

- Information about the connection concerned (origin and destination),

- Any other relevant information permitting quick repair actions and failure analysis.

      - Remote Diagnostic Tests

        - Remote diagnostic tests in the case of an equipment failure shall be possible from the control terminals via the maintenance and control system.

        - The results shall be displayed on a TCT and be recorded in the log.

        - This diagnostic shall be able to trace a failure up to Line Replaceable Unit level.

      - The System monitoring and control facility shall be able generate on request reports about System statuses (system operational, system malfunctions, system failures, etc.) during selected period at least 5 months in the past.

Technical Requirements

  - System Architecture and Technology

    - The System design shall be based upon the application and adaptation of proven modern technology and architecture (hardware and software) with the objective of optimizing overall system performance over the lifetime, minimising technical risks, and meeting the safety requirements of the user.

    - The technology utilised shall meet the requirements for a System that is reliable and resilient to failure. In addition, the technology shall support the requirements for rapid communications and a high degree of flexibility.

    - It is imperative that all hardware, software, and firmware that is to be utilized shall be totally proven in an operational environment that has similar, if not more stringent requirements than those stated within this Specification.

    - In particular, the design of the System shall be such that failure of units shall never cause a complete outage of the total system.

    - The internal architecture of the System shall be based on IP/Ethernet technology and shall meet the operational, reliability, maintainability, availability, and performance requirements as stated throughout this Specification.

    - The System shall comply with EUROCAE WG-67 defined requirements ED-136 of using Voice over Internet Protocol (VoIP) for providing ATM voice services and ED-137C Interoperability standards for VoIP ATM Components.

    - Between VoIP components required interfaces shall be defined to guarantee their functional and technical interoperability.

    - The System architecture shall ensure there are a sufficient number of simultaneous voice paths to carry the maximum offered voice traffic and therefore shall not block any offered voice traffic due to the lack of voice paths.

    - The System shall be able to adapt to changes in the number of terminals and lines, changes in the volume and type of voice traffic and configuration changes.

    - There shall be no degradation in System performance, and any on-line changes shall be implemented without disruption to unaffected system elements.

    - The System to be offered central part shall be server based, and the operator (controller) positions shall be modular in design to be adaptable in the event of re-arrangements of positions, frequency channels and functions. It shall also be flexible in its channel-to-position allocation part.

  - System Software

    - The software shall be designed to provide reliability, error detection, fault tolerance and recovery. To achieve these requirements, it is envisaged it shall be necessary to provide redundant software for essential functions and duplicated storage of programs and data.

    - The System software architecture shall be such that is able to provide the necessary functional and technical parameters according to these requirements.

    - The Operating System software shall provide the capability for real-time execution, file management, command procedures and various utilities.

    - The application software shall include software that is unique to a specific function, for example, call processing or call control.

    - The System configuration data shall consist of all details of variables and configuration parameters of the System.

    - The System maintenance software shall be available when the system requires reports on diagnostics, testing, etc. This software shall run in background and shall have no detrimental effect on any system processing.

    - The system maintenance software shall provide self-diagnostic capabilities, with the ability to detect failures, and automatically or with operator intervention isolate any defective parts and take out of service any defective communication path or communication link.

    - The system maintenance software shall include facilities for activity and event logging. It shall be possible to extract this information from the system in a suitable format, for offline statistical analysis, for evidence of system operation for a certain period of time without in any way effecting the operational service.

    - The software design shall be functionally and operationally modular to:

- facilitate system expansion, modification, and configuration control,

- facilitate fault detection, diagnosis, containment, recovery, and fault tolerance,

- facilitate changes to the lowest practical level without large scale program re-assemblies,

- allow all configuration data to be held in separate data files.

  - Reliability and Availability

    - The system shall provide all required communication functions for the control centre for 24 hours a day, seven days a week since no air traffic control unit can afford to ever be deprived of communication.

    - The availability of the system shall be 99,999% or better.

    - To achieve the required degree of reliability, duplication of system units with automatic switchover and fault indication as well, as decentralisation of system functions, avoiding a single point of failure shall be considered.

    - Supplier shall specify MTBF values of whole system and functional parts of the system.

  - System Design

    - The System design and construction shall be based on IP technology.

    - All System components shall be interconnected via internal redundant network, which shall be protected from external network to avoid cyber threats.

    - To ensure high availability and reliability of the System operation dual internal network and dual servers, routers, switches shall be used.

    - Faults in one unit shall thus never influence the proper operation of other units.

    - All the System services and components shall be fully manageable and System performance quality shall be controlled constantly.

  - Maintainability

    - Suitable means of self-diagnostics to ensure rapid fault detection and isolation shall be anticipated.

    - Automatic or manual (off-line) testing of routines shall be capable. Faulty units shall thus be immediately identified and shall be easily replaceable.

  - Safety Requirements

    - System Safety Assessment

      - During the process of the System implementation the Supplier shall carry out safety assessment of the System and shall prepare functional hazard assessment (FHA), preliminary system safety assessment (PSSA) and system safety assessment (SSA) documents.

    - Software Safety Assessment

      - Required System software assurance level shall be SWAL4 or better according to EUROCAE ED-153.

      - Supplier shall provide an assessment of compliance with the applicable software assurance level.

    - Equipment Safety

      - The System equipment shall be designed to meet the requirements of EN 62368-1:2014 - Audio/video, information and communication technology equipment - Part 1: Safety requirements.

  - Electromagnetic Compatibility (EMC)

    - System equipment shall meet the general requirements for EMC imposed by Directive 2014/30/EU of the European Parliament and of the Council of 26 February 2014 on the harmonisation of the laws of the Member States relating to electromagnetic compatibility (recast).

    - System equipment shall also be capable of operating in the proximity of high-power radar transmitters.

  - Voice Quality

    - The speech quality using VoIP in an ATM environment is an important aspect from the user perception as well as technical requirements on transmission characteristics and shall meet ED-136 Voice over Internet Protocol (VoIP) Air Traffic Management (ATM) System Operational and Technical Requirements, chapter 6.

    - The system shall achieve a Mean Opinion Score (MOS) > 4.0 for all air-ground and ground-ground communications.

    - The system shall ensure that during any communication, the User’s own echo is within the acceptable area of the ITU-T G.131 recommendation for both telephone (reflected echo) and radio (sidetone).

    - The voice delays through any interface of the System shall not exceed the values described in ED-136 Voice over Internet Protocol (VoIP) Air Traffic Management (ATM) System Operational and Technical Requirements.

    - The audio background noise level in earpiece of the headset or handset, or loudspeaker generated by the voice communication system with no input signal to the system shall be as low as it is possible and shall be specified in the Offer.

Note: The existing VCS has a fairly noticeable background noise that shall be avoided in the new System.

  - Telephone Communication

    - System shall be equipped with telephony interfaces for interconnection with IP based PABX or PSTN and for interconnection with IP based System according to EUROCAE ED-137C via AGVN.

    - The number of required telephone connections is specified in Annex 3.

    - The System shall support the following user numbering and addressing schemes:

- ETSI EN 300 189 V1.2.1, Private Integrated Services Network (PISN); Addressing,

- EUROCONTROL “ATS Ground Voice Network Implementation and Planning Guidelines”,

- EUROCONTROL “Session initiation protocol addressing in ATM VoIP”,

- ICAO “Manual on Air Traffic Services (ATS) Ground-To-Ground Voice Switching and Signalling” (Doc 9804 AN/762),

- Mnemonic Addressing Scheme based on relevant ATS information (User, ATS sector, ATS radio frequency, ATS radio site, ATSU, ICAO site identifier, ANSP or ATS Organisation).

    - Each extension user may be allocated one or more unique numbers within the scope of the System numbering scheme.

  - Radio Control System

    - The operation of the radio control system shall be simple and straightforward. For any frequency channel selected at a frequency activation module, a permanent connection through the system inside the centre shall be established.

    - The radio interfaces shall be the link between the System radio control system and the radios. The radio interfaces take care of the complete communication for the radio channels involved and shall perform the following functions:

- Interconnection the System to VoIP radios via an IP network according to ED-137C,

- handle the transmission of keying and audio signals from the working positions to the transmitters,

- handle the reception of audio and squelch signals from the receivers,

- handle the transmissions in both directions of data concerning status indications, switching commands.

    - Radio interfaces shall support redundant connectivity to the main and standby radios.

  - Supporting Facilities and Interfacing to the Supporting Facilities

    - Connection Check

      - The system shall provide means to automatically ensure all telephone and radio interconnections are operational and ready for use.

      - The system shall check, continuously, that both telephone and radio call setups are possible to all ATSU and Transmitter/Receiver locations that have been configured, such that any end-to-end connection loss to these locations shall be detected within 3 seconds and the event noted by the System Management facility within that time.

    - Secure External Connections

      - Session Border Controller (SBC) constitute a key element to enhance security and availability of VoIP in ATM interconnections between ANSPs via IP networks for the provision of inter-centre telephony and for the ground segment of voice radio communications.

      - System shall be equipped with SBC facility according to Eurocontrol implementation guidelines – Session border controller in ATM VoIP.

    - Legal Voice Recording

      - Voice recording of all communications at OWP level shall be available on external ReDat voice recorder of the Customer and shall be IP based and meet ED-137C requirements for recording.

      - The System shall provide a means by which two autonomous voice recordings can be made. Both recordings shall be identical in all respects.

      - For the purposes of imprinting date and timestamp information with the recorded voice (to enable the time and date of re-played voice messages to be precisely identified), the System shall be synchronous with the date and time data source.

    - Power Supply

      - The System servers, network devices and OWPs shall be fed from two independent 230 V and 50 Hz AC power supply lines. These power inputs will interface with an uninterruptible power supply (UPS) units provided by the Customer.

      - The cabinet 19-inch wide will be provided by the Customer, where central System units shall be installed. It will be equipped with 2 power distribution units (PDU), which allows distribution of the redundant power supply inside the cabinet.

    - Central Time Source

      - The System shall be supplied with the Time Reference System (Clock System) GNSS (Multi-Constellation) synchronized.

      - The system shall be synchronized with trusted time sources. At least two independent time synchronization sources must be used.

  - Environmental Conditions

    - The System shall keep normal functionality within nominal operational conditions – temperature range from +10°C to +40°C, humidity up to 80%.

Training

  - Supplier shall provide technical and operational training for the Customers personnel. The training content shall be aligned with the roles and responsibilities of the intended user groups.

  - Language of the training and training material shall be Lithuanian or English.

  - Technical Training

    - Technical training shall be provided at the Supplier’s premises before Factory Acceptance Testing (FAT) for dedicated Customers technical personnel up to 8 attendees.

    - Duration of the technical training shall be of at least 40 hours to cover theoretical course, covering standards and technologies employed in the System, system architecture, composition, configuration, maintenance and fault detection, as well practical training to provide system configuration, reconfiguration, maintenance, and troubleshooting.

    - The Supplier shall send the training program to the Customer for review at least 3 weeks before the training date. The Customer shall be allowed to do corrections of the training program If the Customer expresses a desire to adjust the training program, the supplier will have to take this into account.

    - Each training attendee shall be supplied with the training material.

    - The technical training attendees shall be tested after the training and shall receive the training certificates with test results.

  - Operational Training

    - Supplier shall organize operational training at the Customer’s premises after a successful Site Acceptance Testing (SAT) – 2 groups in Kaunas site, 2 groups in Palanga site, and 4 groups in Vilnius site. Each group could contain up to 12 attendees.

    - Operational training shall cover theoretical course and practical exercises how to use all devices of the OWP, how to organize, establish and control all possible communications. Each training attendee shall be supplied with the training documentation.

    - After successful training completion operational training attendees shall receive the certificates.

Spare Parts

  - The Supplier shall offer necessary spare parts, modules, devices, etc. for replacement of faulty parts on site by the Customer’s technical personnel.

  - Additionally spare HMIs, headsets, handsets, and hand microphones shall be offered. The preferred number of audio devices is specified in Annex 1.

Delivery

  - The Supplier shall deliver the System to the Customer after successful completion of the FAT under CIP conditions according to INCOTERMS 2020.

  - Delivery address is Oro navigacija, Balio Karvelio str. 25, Vilnius, Lithuania.

System Installation

  - Installation Conditions

    - The Customer will provide 19-inch-wide cabinet with redundant power supply for central System part installation.

    - The Customer has its own country wide FO network (ring between sites), which shall be used by the Supplier to establish necessary connections between System cabinet in Vilnius and all sites with OWPs, radios, PABX and PENS access point.

    - The Customer will be liable to allocate spaces in racks or cabinets for the System equipment installation in Vilnius, Kaunas, and Palanga sites.

    - The Customer will be liable for installation of dual 230 VAC power supply in cabinets at the installation sites terminated with the IEC C13 female connectors.

    - The Supplier shall connect System equipment into IEC C13 female connectors of the power supply.

    - The Supplier shall do System installation works during the working hours of the employees of the Customer, i.e., from Monday to Thursday (not on public holidays) from 07:30 to 16:15 and on Fridays (also on the eves of public holidays) from 07:30 to 15:00.

  - Installation Works

    - The Supplier shall install delivered System. Installation shall be done in following Customer’s places:

- The System Cabinet shall be installed in the Equipment Room of the main building of Oro navigacija, Balio Karvelio str. 25, Vilnius, Lithuania,

- Operator working positions shall be installed in places as described in Annex 1.

    - The Supplier shall implement double LAN cabling:

      - at Vilnius main site:

- between System Cabinet and OWPs of ACC (11), FIS (4), FMP (1), FDO (1), RCC (1), TCS (1), TTP (1),

- between System Cabinet and the Customer’s IP network access point,

- between the Customer’s IP network access point and TCT in the Technical Control Service room.

      - at Vilnius rTWR site:

- between the Customer’s IP network access point in rTWR technical room and 5 OWPs: rAPP, rTWR, rTWR2, rSMC and rAPP/TWR SUP.

      - at Vilnius TWR site:

- between the Customer’s IP network access point in TWR technical room and 7 OWPs: APP, TWR, TWR2, SMC, APP/TWR SUP, BRF and BRF2.

      - at Kaunas TWR site:

- between the Customer’s IP network access point in Kaunas technical room and OWPs: APP, TWR, TWR2, APP/TWR SUP,

- between the Customer’s IP network access point in Kaunas technical room and both OWP TCS and TCT in the Technical Control Service room.

      - at Palanga TWR site:

- between the Customer’s IP network access point in Palanga technical room and OWPs: APP, TWR, APP/TWR SUP,

- between the Customer’s IP network access point in Palanga technical room and both OWP TCS and TCT in the Technical Control Service room.

    - Twisted pair Ethernet and Fiber Optic (FO) lines are equally acceptable for LAN cabling.

    - The Supplier shall include in the supply list all the necessary network devices to interconnect the System with all OWPs and Customer’s IP network access points.

    - All internal system cables shall be labelled in both ends and the cable list shall be added to the system description.

System Tests

  - Factory Acceptance Testing (FAT)

    - The fully equipped System in its initial configuration shall be tested at the factory to demonstrate for the Customer’s representatives how the system meets all the specified requirements. The Supplier shall issue FAT procedure and coordinate it to the Customer at least two weeks before FAT. Testing shall be performed according to agreed FAT procedure.

    - The Supplier shall provide a formal declaration confirming that there are no vulnerabilities have in the system or presenting a formal remediation plan addressing all identified vulnerabilities, including clear timelines and responsibilities for fixing them.

    - A second vulnerability assessment shall be conducted during the SAT. The system shall only be accepted if no critical ir high-severity vulnerabilities or any identified medium or low severity vulnerabilities which pose unacceptable risks to the system’s security, safety or operation, as determined by the Customer or independent the third party, are present at this stage.

    - The System’s testing results shall be presented in the FAT certificate and signed by both parties.

    - FAT testing acceptance criteria shall comply with these requirements:

      - There are no priorities 1 and priorities 2 faults.

      - 93% of Test Steps are Passed.

      - All comments raised in the formal test activity are closed or there is an agreed plan to close them.

      - There is an agreed plan and time frame to fix detected priority 3 faults.

      - Vulnerability scanning/penetration testing performed and a formal remediation plan addressing all identified vulnerabilities, including clear timelines and responsibilities for fixing them. The remediation plan shall be reviewed and accepted by Customer.

    - In case, if according to FAT procedure at least one or more of the System tests fails, these non-conformances and their correction terms shall be noted in the FAT certificate. The Supplier shall fix all System non-conformances according to the set terms and report to the Customer via email about the elimination of these non-conformances. All the non-conformances have to be corrected before SAT.

  - Site Acceptance Testing (SAT)

    - Properly installed and configured System on site shall undergo acceptance testing to demonstrate that System operates in accordance with the specifications outlined in this document and is suitable for operation without remarks.

    - The Supplier shall present SAT procedure to the Customer at least two weeks before testing to coordinate and agree by both parties.

    - SAT testing acceptance criteria shall comply with these requirements:

      - There are no priorities 1 and priorities 2 faults.

      - 97% of Test Steps are Passed.

      - All comments raised in the formal test activity are closed or there is an agreed plan to close them.

      - There is an agreed plan and time frame to fix detected priority 3 faults and achieve 100% of Test Steps rate.

      - Reassessed vulnerability scanning/penetration testing performed and no critical or high-severity vulnerabilities (as determined by Customer or independent third party) remain unresolved. The Manufacturer has provided a formal written declaration confirming the remediation of all critical or high-severity vulnerabilities.

      - Any identified medium or low severity vulnerabilities do not pose unacceptable risks to the system’s security, safety or operation, and a Manufacturer provided remediation plan with agreed timelines is in place.

    - After successful site testing, the SAT certificate shall be signed by both parties. If at least one or more non-conformances to the SAT procedure are found during the on-site tests, this shall be recorded in the SAT certificate, where it shall be indicated how long the non-conformities will be corrected.

    - If the system non-conformity is significant, preventing proper use of the system, the SAT certificate should not be signed until it is corrected. If the non-conformity is not significant, then it can be signed, indicating the remaining uncorrected non-conformities and the deadlines for their elimination in the SAT certificate.

    - If site testing fails, if at least one essential error is detected that prevents the proper use of the system for its intended purpose, Supplier shall fix System malfunctions according to the term agreed by both parties, within 30 calendar days and shall repeat the tests again. In such case, additional SAT is carried out at the Supplier's expenses.

System Warranty and Lifetime

  - The warranty period of the System hardware and software shall be at least 24 months. The warranty period shall begin from the date of signature of the Transfer and Acceptance Act by both parties after the System installation and signature of SAT certificate.

  - During the warranty period the Supplier shall provide at its own expenses technical support and repair services of the System.

  - The Supplier shall declare System lifetime it shall be long enough but at least 10 years.

Warranty Support

  - During warranty period of System, the Supplier shall undertake the liability to provide System hardware (including firmware) repair service (HRS) and System software support service (SWS).

  - HRS provision

    - Having identified System hardware failures, the Customer shall notify the Supplier about the failure in written.

    - The Supplier shall notify the Customer about the readiness to receive the faulty part in written not later than within 2 working days from the written notification of the Customer and shall grant the Customer a number for the repair order.

    - Having received the repair order number, the Customer shall ship the faulty part to the Supplier and shall notify him about the shipment in written. The shipment expenses shall be covered by the Customer.

    - The Supplier shall deliver the repaired or, in case if the part is irreparable, the new part to the Customer not later than within 30 calendar days. The part return expenses shall be covered by the Supplier.

    - HRS is considered completed when the Customer receives the part, tests it, and gets positive result.

  - SWS provision

    - When providing the SWS service the Supplier shall undertake the liability to provide support by solving the System software operational problems and ensuring smooth operation of System software on Supplier’s working hours.

    - The Customer shall notify the Supplier in written about System software operation failures.

    - The Supplier shall notify the Customer in written not later than within 2 working days after the notification from the Customer about the SWS service: (1) method of delivery, (2) works necessary to be done, (3) work completion terms.

    - The Supplier shall be liable to provide the SWS service not later than within 5 working days from the notification about operational failures.

    - SWS shall be considered provided, when the Customer confirms in written that the System operates properly.

After Warranty Support

  - After the end of warranty period of System, the Supplier shall undertake the liability to provide System hardware repair services (HRS), supply new parts (when used faulty parts are irreparable, or the repair is not cost-efficient) and System software support services (SWS) for period up to 120 months from the System SAT.

  - The HRS and SWS services shall be procured only when the need arises and shall not exceed the maximum sum allocated for the acquisition of the respectful services. Hourly rates for HRS and SWS services shall be offered.

  - Having identified System hardware failures, the Customer shall undertake the liability to procure HRS (or new parts) in accordance with need, submitting orders to the Supplier pursuant to the following procedure:

    - The Customer shall notify the Supplier about the failure in written.

    - The Supplier shall notify the Customer about the readiness to receive the faulty part in written not later than within 2 working days from the written notification of the Customer and shall grant the Customer a number for the repair order or, in case the faulty part is irreparable, shall notify the Customer about it in written.

    - Having received the repair order number, the Customer shall ship the faulty part to the Supplier and shall notify him about the shipment in written.

    - The Supplier shall assess the malfunction and provide the repair price offer in written not later than within 5 working days from the reception of the malfunctioning part. At the request of the Customer, the Supplier shall be liable to submit repair price justification.

    - The Customer shall evaluate the received information and shall notify the Supplier in written, whether the Customer is willing to repair the faulty part or the part must be replaced with a new part after the Supplier indicates the price of the new part (in case the Supplier does not indicate the price of the new part – at the rates indicated in the sales location, catalogue or internet website of the Supplier or, in case they are not published, at the rates offered by the Supplier and acceptable to the Customer). In all the cases the equipment or part thereof repair price, or the new part price shall be coordinated with the Customer in advance in written. The equipment or part thereof repair price must not be higher than the price of the same new part.

    - In case the part thereof is no longer manufactured, and it cannot be repaired or replaced, the Supplier shall be liable to offer replacing the faulty part thereof with an equivalent. In case of instant malfunctioning of the server, which was installed and operating in high reliability mode, in order to ensure full compatibility, the entire set (2 units) must be replaced.

    - Not later than within 30 calendar days from the confirmation of the order of the Customer, i.e., from written confirmation to repair the malfunctioning part or the day of ordering the new part, the Supplier shall deliver the repaired or new part to the Customer. Along with the delivered part or using the e-mail the Supplier shall provide the Customer with a note on transfer and acceptance of the repair services or new part transfer. The part shipment and return expenses shall be covered by the Customer.

    - HRS shall be considered provided, when the Parties sign the act on transfer and acceptance of the services.

    - The Customer shall be entitled to revoke the order by notifying the Supplier about it in written before the written confirmation of the Customer regarding the repair of the faulty part without reimbursing any expenses incurred by the Supplier.

    - The Supplier shall grant a warranty of 6 months to repaired parts. The warranty term shall be calculated from signing the act on transfer and acceptance of the services. In case the repair has been performed improperly, the Supplier shall be liable to eliminate the identified deficiencies during the warranty term (i.e. to repair the equipment or part or provide a new analogue) at own expense not later than within 35 days from the day of sending a written notification about the deficiencies to the Supplier. The part delivery expenses shall be covered by the Supplier.

    - The Supplier shall grant a warranty of 24 months for the new parts. The warranty period shall be calculated from the day of reception new part, i.e., from signing the act on transfer and acceptance. The part with defects or deficiencies identified during the warranty period shall be replaced free of charge with new part not later than within 30 days from the day of shipping a written notification of the Customer about the deficiencies to the Supplier. The part shipment expenses shall be reimbursed by the Supplier.

  - When providing the SWS service the Supplier shall undertake the liability to provide support by solving the System software operational problems and ensuring smooth operation of System software on Supplier’s working hours.

  - Having identified System software operation problems, the Customer shall procure the SWS service in accordance with the need pursuant to the following procedure:

    - The Customer shall notify the Supplier in written about System software operation failures.

    - The Supplier shall notify the Customer in written not later than within 2 working days after the notification from the Customer about the need of SWS service: (1) method of delivery, (2) SWS works necessary to be done, (3) work completion terms, (4) the SWS service price, in accordance with the established rate.

    - Having evaluated the offer of the Supplier regarding the SWS services, the Customer shall notify the Supplier in written, whether the Customer agrees with the submitted offer (in case of disagreement – shall indicate the reasons). The Supplier shall be liable to submit another offer for the provision of the SWS service within 5 working days from the disagreement of the Customer, which would be acceptable for the Customer, and the Customer shall be liable to notify the Supplier about the consent.

    - SWS shall be considered provided, when the Parties sign the act on transfer and acceptance.

Documentation

The following System documentation shall be supplied in electronic, editable format (e.g. .docx, .xlsx, .pptx or other commonly used formats that support content modification):

  - System Description, including a current logical network and system infrastructure, as well as a detailed network and system architecture diagram (these diagrams must accurately reflect the implemented solution and be updated promptly whenever changes occur).

  - System Specification (detailed).

  - Interface Control Document.

  - Installation Manual (including detailed information and schematics of power supply and network interconnections).

  - Configuration Manual.

  - Maintenance Manual.

  - Control and Monitoring Manual.

  - User Manual.

  - Training Materials.

  - Software Licenses (If applicable).

  - Testing documentation.

  - Remediation plan for identified vulnerabilities (if they exist).

Project management

  - Not later than within 30 days since the Contract comes into force the Supplier shall be liable to prepare and coordinate with the Customer project management (System Installation) plan, which shall specify the following:

    - Project goals, priorities.

    - Scope and results of the milestones.

    - Work execution schedule.

    - Risks and methods for managing them.

    - Communication principles.

    - Liabilities.

    - The Supplier shall propose acceptance criteria for interim and final deliverables, subject to the Client’s approval.

    - Plan correction and change management procedure and their execution term.

    - Problem solving procedure.

- Note: 	The work execution schedule can be amended under the agreement of the parties, by amending the interim System installation terms, nevertheless, the final System installation and transfer to the Customer term cannot be changed (extended), except for term extension cases established under the Contract, provided that they are defined.

  - The Supplier shall be liable to prepare and provide the Customer with project execution course (System installation) report at certain regularity (for example, every quarter, half a year) agreed upon by the parties and established under System Installation Plan.

References

  - ICAO Convention on International Civil Aviation, Annex 10, Volume III, Part II, Chapter 4: Aeronautical Speech Circuits.

  - ICAO Convention on International Civil Aviation, Annex 11, Chapter 6: Air Traffic Services Requirements for Communications.

  - ICAO Manual on Air Traffic Services (ATS) Ground-To-Ground Voice Switching and Signalling (Doc 9804 AN/762).

  - EN 300 189: Private Integrated Services Network (PISN); Addressing.

  - ISO/IEC 7498-4: Information processing systems - Open Systems Interconnection - Basic Reference Model - Part 4: Management framework.

  - ISO/IEC 11573: Information technology - Telecommunications and information exchange between systems - Synchronization methods and technical requirements for Private Integrated Services Networks.

  - EUROCAE ED-153 Guidelines for ANS Software Safety Assurance.

  - EUROCAE ED-136 Voice over Internet Protocol (VoIP) Air Traffic Management (ATM) System Operational and Technical Requirements.

  - EUROCAE ED-137C Interoperability Standards for VoIP ATM Components.

  - Eurocontrol implementation guidelines – Session border controller in ATM VoIP.

  - Commission Delegated Regulation (EU) 2023/1768 of 14 July 2023 laying down detailed rules for the certification and declaration of air traffic management/air navigation services systems and air traffic management/air navigation services constituents.

  - EASA Detailed Specifications and Acceptable Means of Compliance & Guidance Material for certification or declaration of design compliance of ATM/ANS ground equipment (DS-GE.CER/DEC).

  - EN 62368-1:2014 - Audio/video, information and communication technology equipment - Part 1: Safety requirements.

  - Directive 2014/30/EU of the European Parliament and of the Council of 26 February 2014 on the harmonisation of the laws of the Member States relating to electromagnetic compatibility (recast).

Annex 1

| Description of OWPs |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Name, role | Control and audio devices |  |  |  |  |
|  |  | HMI type | Loudspeaker | Hand- held phone | Headset (monoaural) | Hand-held microphone |
| Kaunas APP/TWR |  |  |  |  |  |  |
| 1 | APP | Desktop | 2 | 1 | 1 | 1 |
| 2 | TWR | Desktop | 2 | 1 | 1 | 1 |
| 3 | TWR2 | Desktop | 2 | 1 | 1 | 1 |
| 4 | APP/TWR SUP | Desktop | 2 | 1 | 1 | - |
| 5 | TCS | Desktop | 2 | 1 | 1 | - |
| Palanga APP/TWR |  |  |  |  |  |  |
| 6 | APP | Desktop | 2 | 1 | 1 | 1 |
| 7 | TWR | Desktop | 2 | 1 | 1 | 1 |
| 8 | APP/TWR SUP | Desktop | 2 | 1 | 1 | - |
| 9 | TCS | Desktop | 2 | 1 | 1 | - |
| Vilnius APP/TWR/BRF |  |  |  |  |  |  |
| 10 | APP | Desktop | 2 | 1 | 1 | 1 |
| 11 | TWR | Desktop | 2 | 1 | 1 | 1 |
| 12 | TWR2 | Desktop | 2 | 1 | 1 | 1 |
| 13 | SMC | Desktop | 2 | 1 | 1 | 1 |
| 14 | APP/TWR SUP | Desktop | 2 | 1 | 1 | - |
| 15 | BRF | Desktop | 2 | 1 | - | - |
| 16 | BRF2 | Desktop | 2 | 1 | - | - |
| Vilnius rAPP/rTWR |  |  |  |  |  |  |
| 17 | rAPP | Desktop | 2 | 1 | 1 | 1 |
| 18 | rTWR | Desktop | 2 | 1 | 1 | 1 |
| 19 | rTWR2 | Desktop | 2 | 1 | 1 | 1 |
| 20 | rSMC | Desktop | 2 | 1 | 1 | 1 |
| 21 | rAPP/TWR SUP | Desktop | 2 | 1 | 1 | - |
| Vilnius ACC/FIS/FMP/RCC |  |  |  |  |  |  |
| 22 | ACCU | Desktop | 2 | 1 | 1 | 1 |
| 23 | ACCU2 | Desktop | 2 | 1 | 1 | 1 |
| 24 | ACCM | Desktop | 2 | 1 | 1 | 1 |
| 25 | ACCM2 | Desktop | 2 | 1 | 1 | 1 |
| 26 | ACCL | Desktop | 2 | 1 | 1 | 1 |
| 27 | ACCL2 | Desktop | 2 | 1 | 1 | 1 |
| 28 | ACCE | Desktop | 2 | 1 | 1 | 1 |
| 29 | ACCE2 | Desktop | 2 | 1 | 1 | 1 |
| 30 | ACC Rez | Desktop | 2 | 1 | 1 | 1 |
| 31 | ACC Rez2 | Desktop | 2 | 1 | 1 | 1 |
| 32 | ACC SUP | Desktop | 2 | 1 | 1 | - |
| 33 | FIS Vilnius | Desktop | 2 | 1 | 1 | 1 |
| 34 | FIS Kaunas | Desktop | 2 | 1 | 1 | 1 |
| 35 | FIS Šiauliai | Desktop | 2 | 1 | 1 | 1 |
| 36 | FIS Palanga | Desktop | 2 | 1 | 1 | 1 |
| 37 | FMP | Desktop | 2 | 1 | - | - |
| 38 | FDO | Desktop | 2 | 1 | - | - |
| 39 | RCC | Desktop | 2 | 1 | - | - |
| 40 | TCS | Desktop | 2 | 1 | 1 | 1 |
| 41 | TTP | Mounted into cabinet | 2 | 1 | 1 | 1 |
| In the working positions: |  | 41 | 82 | 41 | 36 | 29 |
| Spare: |  | 4 | 8 | 20 | 15 | 6 |
| Total: |  | 45 | 90 | 61 | 51 | 35 |

Annex 2

| Radio channels, equipment, and sites |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Name | Channel | Tx | Rx | TRx | Location of radios |
|  | Vilnius ACC |  |  |  |  |  |
| 1 | ACCU_KAU | 132.280 | M/S | M/S | - | Kaunas |
| 2 | ACCU_VIL | 132.280 | M/S | M/S | - | Vilnius |
| 3 | ACCU_PAL | 132.280 | M/S | M/S | - | Palanga |
| 4 | ACCL_KAU | 133.305 | M/S | M/S | - | Kaunas |
| 5 | ACCL_VIL | 133.305 | M/S | M/S | - | Vilnius |
| 6 | ACCL_PAL | 133.305 | M/S | M/S | - | Palanga |
| 7 | ACCM_KAU | 133.430 | M/S | M/S | - | Kaunas |
| 8 | ACCM_VIL | 133.430 | M/S | M/S | - | Vilnius |
| 9 | ACCM_PAL | 133.430 | M/S | M/S | - | Palanga |
| 10 | ACCE_VIL | 135.380 | M/S | M/S | - | Vilnius |
| 11 | EMG | 121,500 | M/S | M/S | - | Vilnius |
| 12 | ATIS | 125.805 | - | M | - | Vilnius |
|  | Vilnius FIS |  |  |  |  |  |
| 1 | FIS Vilnius | 123.855 | M/S | M/S | M/S | Vilnius, Utena, Alytus |
| 2 | FIS Kaunas | 124.605 | M/S | M/S | M/S | Kaunas, Kazlų Rūda |
| 3 | FIS Siauliai | 124.455 | M/S | M/S | M/S | Šiauliai, Panevėžys |
| 4 | FIS Palanga | 125.730 | M/S | M/S | M/S | Palanga, Telšiai, Šilutė |
|  | Vilnius RCC |  |  |  |  |  |
| 1 | RCC Vilnius | 123,100 | M/S | M/S | - | Vilnius |
| 2 | RCC Kaunas | 123,100 | M/S | M/S | - | Kaunas |
| 3 | RCC Palanga | 123,100 | M/S | M/S | - | Palanga |
|  | Vilnius APP/TWR |  |  |  |  |  |
| 1 | APP | 120.705 | M/S | M/S | - | Vilnius |
| 2 | TWR | 118.205 | M/S | M/S | - | Vilnius |
| 3 | SMC | 121.805 | M/S | M/S | - | Vilnius |
| 4 | EMG | 121,500 | M/S | M/S | - | Vilnius |
| 5 | ATIS | 125.805 | - | M | - | Vilnius |
|  | Vilnius rAPP/rTWR |  |  |  |  |  |
| 1 | APP | 120.705 | M/S | M/S | - | Vilnius |
| 2 | TWR | 118.205 | M/S | M/S | - | Vilnius |
| 3 | SMC | 121.805 | M/S | M/S | - | Vilnius |
| 4 | EMG | 121,500 | M/S | M/S | - | Vilnius |
| 5 | ATIS | 125.805 | - | M | - | Vilnius |
|  | Kaunas APP/TWR |  |  |  |  |  |
| 1 | APP | 124.205 | M/S | M/S | - | Kaunas |
| 2 | TWR | 118.505 | M/S | M/S | - | Kaunas |
| 3 | SMC | 121.605 | M/S | M/S | - | Kaunas |
| 4 | ATIS | 129.055 | - | M | - | Kaunas |
| 5 | EMG | 121,500 | M/S | M/S | - | Kaunas |
|  | Palanga APP/TWR |  |  |  |  |  |
| 1 | APP | 124.305 | M/S | M/S | - | Palanga |
| 2 | TWR | 118.305 | M/S | M/S | - | Palanga |
| 3 | SMC | 121.905 | M/S | M/S | - | Palanga |
| 4 | ATIS | 127.805 | - | M | - | Palanga |
| 5 | EMG | 121.500 | M/S | M/S | - | Palanga |
| 6 | FIS | 125.730 | - | - | M/S | Palanga, Telšiai, Šilutė |
| Additional channels to the radios of neighbour ANSP partners and for internal development - 10 radio channels. |  |  |  |  |  |  |

Annex 3

| VoIP telephone connections |  |  |  |  |
| --- | --- | --- | --- | --- |
| No of Positions | Connection | Network | Protocol | Notes |
| Vilnius ACC/FIS/RCC |  |  |  |  |
| 20 | NewPENS | AGVN | ATS-SIP |  |
| 20 | PABX | LAN | SIP | (Or PSTN SIP) |
| Vilnius APP/TWR/BRF |  |  |  |  |
| 7 | NewPENS | AGVN | ATS-SIP |  |
| 7 | PABX | LAN | SIP | (Or PSTN SIP) |
| Vilnius rAPP/rTWR |  |  |  |  |
| 5 | NewPENS | AGVN | ATS-SIP |  |
| 5 | PABX | LAN | SIP | (Or PSTN SIP) |
| Kaunas APP/TWR |  |  |  |  |
| 5 | NewPENS | AGVN | ATS-SIP |  |
| 5 | PABX | LAN | SIP | (Or PSTN SIP) |
| Palanga APP/TWR |  |  |  |  |
| 4 | NewPENS | AGVN | ATS-SIP |  |
| 4 | PABX | LAN | SIP | (Or PSTN SIP) |
| Connections Totally | NewPENS - 41 |
|  | PABX - 41 |

Annex 4

Centralized Voice Communication System Possible Architecture

Abbreviations

A/C	– Aircraft

A/G	– Air-Ground

ACC	– Area Control Centre

ACCL	– Area Control Centre Lower Airspace Controller position

ACCL2	– Area Control Centre Lower Airspace Controller Assistant position

ACCM	– Area Control Centre Middle Airspace Controller position

ACCM2	– Area Control Centre Middle Airspace Controller Assistant position

ACCU	– Area Control Centre Upper Airspace Controller position

ACCU2	– Area Control Centre Upper Airspace Controller Assistant position

ACCE	– Area Control Centre Eastern Airspace Controller position

ACCE2	– Area Control Centre Eastern Airspace Controller Assistant position

ACC Rez	– Area Control Centre Spare Controller position

ACC Rez2	– Area Control Centre Spare Controller Assistant position

ACC SUP	– Area Control Centre Supervisor position

AGVN	– Air Traffic Services Ground Voice communications Network

ANS	– Air Navigation Services

APP	– Approach Control or Approach Controller position

ATC	– Air Traffic Control

ATCC	– Air Traffic Control Centre

ATIS	– Aerodrome Terminal Area Information Service

ATM	– Air Traffic Management

ATS	– Air Traffic Services

ATSU	– Air Traffic Services Unit

BSS	– Best Signal Selection

CC	– Common Control

DA	– Direct Access

EMG	– Emergency

FAT	– Factory Acceptance Testing

FIS	– Flight Information Service

FO	– Fiber Optic

G/G	– Ground-Ground

HMI	– Human Machine Interface

HRS	– Hardware Repair Service

IA	– Instantaneous Access

IC	– Intercom or Internal Communications

IDA	– Indirect Access

IP	– Internet Protocol

MBTF	– Mean Time Between Failures

M/S	– Main and Standby

OCT	– Operational Control Terminal

OWP	– Operator (Controller or other) Working Position

PABX	– Private Automatic Branch Exchange

PSTN	– Public Switched Telephone Network

PTT	– Press-to-transmit, or Push-to-talk

R/T	– Radio Telephony

RTP	– Real Time Transfer Protocol

rTWR	– Remote Tower or Remote Tower Controller posistion

Rx	– Receiver

SAT	– Site Acceptance Testing

SBC	– Session Border Controller

SIP	– Session Initiation Protocol

SMC	– Surface Movement Control

SUP	– Supervisor

SWS	– Software Support Service

TCS	– Technical Control Service

TCT	– Technical Control Terminal

TSS	– Touch Sensitive Screen

TTP	– Technical Testing Position

TWR	– Aerodrome Tower or Aerodrome Tower Controller position

TWR2	– Aerodrome Tower Controller Assistant position

Tx	– Transmitter

TRx	– Transceiver

URI	– Uniform Resource Identifier

VCS	– Voice Communication System or System

VoIP	– Voice over Internet Protocol

SWS is a service supporting smooth operation of the software, which comprises solving System software problems, error correction, installation, updating, configuration and other assistance related to the use of the software and problems encountered when using the System with the Software.

The communication shall be carried out by e-mail.

The SWS can be provided by telephone, e-mail, via remote connection or by arriving to the System installation site.

The communication shall be carried out by e-mail.

The SWS can be provided by telephone, e-mail, via remote connection or by arriving to the System installation site.