TECHNICAL SPECIFICATION

- DEFINITIONS AND ABBREVIATIONS

  - ”Client”   shall mean UAB Vilniaus kogeneracinė jėgainė

  - “Service provider” shall mean an economic operator, i.e. a natural person, private legal person, public legal person, other organizations and their subdivisions or a group of such persons with whom the Client concludes a Contract.

  - “Contract” shall mean the Contract concluded between the Service provider and the Client in respect of the Object of the Procurement.

  - “Services” shall mean Boiler cleaning using an explosive gas mixture.

  - “Order” shall mean a written document provided to the Service provider on the basis of the Contract by text message, e-mail and/or through the information system specified by the Client, specifying the quantities, addresses and time limit for quantities of the Services.

- OBJECT OF THE PROCUREMENT

  - Boiler cleaning using an explosive gas mixture.

- SCOPE OF THE OBJECT OF THE PROCUREMENT

  - The preliminary quantities of services shall be shown in Table 1 below:

Table No. 1

| Item No. | Service name | Unit of measure | Preliminary Quantity for the Duration of the Contract |
| --- | --- | --- | --- |
|  | Mobilization * | set | 10 |
|  | Cleaning of superheated surfaces of the boiler steam by means of a controlled explosion of a gas mixture. During operation of the boiler.(Online Cleaning) | shifts ** | 20 |
| 3. | Inspection with high temperature resistant video camera | set | 10 |
| 4. | The cost of additional working hours when working after a shift | hour | 20 |

* Mobilization consists of: Transportation of personnel and equipment, accommodation, site set-up, assembly and disassembly of equipment, securing the work area, coordination meeting, acceptance with the client

** One shift consists of 10 hours.

- PLACE OF THE PROVISION OF THE SERVICES

  - Services are provided: Paneriškių g. 25, Vilnius, Lietuva.

- REQUIREMENTS FOR THE OBJECT OF PROCUREMENT

  - Description of the Object of Procurement

    - Cleaning of boiler steam superheater surfaces using a controlled gas mixture explosion while the boiler is in operation. A water-cooled lance with a special bag is introduced through doors or portholes into the boiler near the heating surface to be cleaned. The bag is inflated and the combustible mixture ignited. The resulting shock waves or vibrations of the tubes and walls dislodge deposits of ash and silt. The quantity and dosage of each gas mixture explosion is dependent on the plant’s general condition and degree of contamination. During Cleaning process Boiler operation shall be not interrupt.

    - During the performance of the Contract, the Service Provider shall provide all the necessary equipment, materials and tools, as well as personal safety equipment required for the performance of the Services.

    - The Service Provider must ensure the safety of equipment and personnel when providing the Services. All boiler cleaning services provided by the Service Provider must not damage the boiler parts.

    - Boiler specifications: Flue gas pass /  Natural circulation boiler  VVVHV.

    - Cleaning services must be provided while the waste boiler is operating, preliminarily 3-4 times a year.

    - The Service Provider must have all the materials and equipment necessary for the provision of the Service.

- PROCEDURE AND TIME LIMITS FOR PERFORMANCE OF SERVICES

  - The services must be provided no later than within the period specified in the Tender of Service Provider and the Contract, which shall not exceed 10 (ten) working days from the date the Order is submitted to the Service Provider.

  - The Service Provider will have to provide the Services to the address specified in Part 4 of the Technical Specifications during the Customer's business hours (I-IV 7.30-16.30 hour V 7.30-15.15 hour).

  - The Services will be provided only in accordance with the individual Orders submitted by the Client during the validity of the Contract.

  - The period of 3 (three) days are set for the Client to accept the provided Services (i.e. to sign the deed of transfer and acceptance of the Service result).

- QUALITY AND REMEDYING DEFICIENCIES

  - The following shall be considered as deficiencies of the Services and/or the Service results:

    - The pressure difference of the boiler overheating (4 runs) will be higher than 3 mbar

    - The pressure behind the bag filter will be lower than -50 mbar.

  - The Client has the right to contact the Service Provider regarding the elimination of deficiencies in the Services and/or the Service results no later than within 7 (seven) days from the date of signing the Service Handover–Acceptance Act or from the date the deficiencies are identified.

  - A period of 7 (seven) days shall be set for the elimination of the deficiencies in the Service results identified by the Client.

- TERMS OF PAYMENT

  - The Client shall pay the Service Provider for the actual high-quality Services provided within 30 (thirty) days from the date of signing the Service Result Handover–Acceptance Act and from the date of receipt of the Invoice.

  - The Service Provider shall submit the invoices for the actual Services provided and the Service Handover–Acceptance Acts to the Client no later than by the 2nd (second) calendar day of the current month.

- DOKUMENTAI DOCUMENTS TO BE SUBMITTED TOGETHER WITH THE PROVIDED SERVICES

  - Service transfer-acceptance act;

  - Filmed material if indoor filming was performed with a high temperature resistant video camera.

The preliminary amount of Services is indicated. During the validity period of the Agreement, the Client has the right to adjust the amount of purchased Services, not exceeding the maximum Agreement price specified in the Agreement. The Customer is not obligated to redeem the entire quantity of the Services or any part thereof.