# TECHNICAL SPECIFICATION

Preparatory study for the technical and software solution of relay protection and automation virtualization (centralization).

## Description of the procurement object

The procurement object is the preparation of a study aimed at comprehensively assessing and formulating recommendations regarding the implementation of virtualization and centralization solutions for Protection and Automation (PA) functions in the Lithuanian electricity transmission network (110–400 kV substations).

## Context and objective of the study

Currently, decentralized digital protection and automation solutions are used in Lithuania, where one or several microprocessor-based Intelligent Electronic Devices (IEDs) operating in accordance with the IEC 61850 standard are used for each substation bay. This preparatory study is intended to comprehensively evaluate and design a technical and software solution for the virtualization and centralization of Protection and Automation (PA) devices, where the protection and automation functions of all substation bays are implemented on one or several servers. Litgrid aims to determine how virtualized and centralized substation PA functions could be implemented in 110–400 kV substations in a technically, legally, and economically viable manner, while ensuring appropriate system reliability, cybersecurity, and compatibility with the existing infrastructure. The study shall include an analysis of the legal framework, an analysis of potential technical solutions available on the market from different manufacturers, identification of technical and cybersecurity requirements according to IEC standards, modelling of the architecture of one selected substation, and evaluation of the interaction between virtualized and physical devices. It is also planned to analyse aspects of data communication, testing (HIL, digital twin), operation and training, as well as to provide an evaluation of the solution lifecycle and a competency map.

## The final objective of the study is to formulate recommendations regarding the actual hardware, architecture, and processes required for the safe and reliable implementation of virtualized and centralized PA and communication solutions (switches, RTU, GNSS, etc.) in the Lithuanian electricity transmission network. The preliminary scope of the study is provided below.

## Terms and abbreviations

The terms and their definitions are provided in Annex 1 “Glossary of Terms”.

- Scope of the study

  - Legal and organisational aspects

    - Assessment of the legal framework: identification of the required amendments and additions to the Rules for Electrical Installations of the Republic of Lithuania in order to enable and regulate the use of virtualized protection and automation devices (e.g., development of new definitions explaining what centralized and virtualized protection and automation are, definition of the devices operating within such solutions and the requirements applicable to them, etc.) in transmission network substations with voltage levels from 110 kV to 400 kV (including 10 kV protection and automation devices used for auxiliary systems and shunt reactors in substations of the aforementioned voltage levels).

    - Competency map: identification of the knowledge required for system operation personnel, PA engineers, and IT/OT engineers. Certification requirements shall be defined, the required competency levels formulated, and responsibility boundaries specified.

    - Evaluation of the costs for installation, operation and maintenance of the solution over a 40-year operational lifecycle for selected substations. The CAPEX and OPEX structure shall be detailed (equipment, licensing, maintenance, training, energy consumption), and sensitivity analysis shall be included considering inflation and equipment replacement cycles.

    - Analysis of how the solution “should” be operated: identification of the required tools (testing equipment, software including the use of a virtual digital twin of the system solution), physical infrastructure, human resources and required qualifications. The lifecycle procedures for maintenance of spare physical components and software shall be defined.

  - Protection and Automation (PA) technical aspects

    - . Analysis of the technical requirements applicable to equipment used for the centralization and virtualization of protection and automation devices and to the physical IED (Intelligent Electronic Device) equipment of the solution in accordance with IEC standards and technical recommendations (IEC 61850, IEC 60255, IEC 60834-1 and others): selection of the substation data network architecture and evaluation of the required reliability criteria (in accordance with IEC 61850 station bus and process bus), requirements for synchronization of real-time data transmission, the need for equipment redundancy, etc.

    - Evaluation of the application of communication logic between virtualized and centralized PA devices and their functions in accordance with IEC 60255 and IEC 61850 requirements for one specific substation scheme (provided after signing of the contract), including communication with other substations (teleprotection signalling, line differential protection).

    - Identification and evaluation of the compatibility of communication technologies with currently operating and currently manufactured microprocessor-based PA devices. This shall include cases where a substation implementing a virtualized and centralized PA solution must communicate with another substation equipped with traditional decentralized microprocessor-based PA devices (teleprotection signalling).

    - The study shall include the architecture of the solution for one substation (substation information is provided in Annex 2) and its analysis, covering: the software of virtualized microprocessor-based PA and communication devices, virtualized PA devices for each bay and their required functions, data network devices and their functions, time synchronization devices for data transmission, and PA and communication devices installed in the outdoor switchyard (in accordance with IEC 61869-13) intended for data acquisition from primary high-voltage equipment (current and voltage measuring transformers, current and voltage measuring sensors, circuit breaker/disconnector/earthing switch drives, etc.).

    - The study shall evaluate the feasibility of using current and voltage measuring sensors compliant with IEC 61869 (active or passive) and Merging Units in outdoor 110 kV and 330 kV switchyards within the solution, as well as their data quality self-monitoring capabilities.

    - The study shall evaluate redundancy and backup solutions for the virtualized and centralized PA system and identify which system availability and accessibility indicators must be ensured and how they should be achieved.

  - IT/OT technical aspects

    - Review of the hardware and software required for the solution. Evaluation of the possibilities for interoperability between different vendors (multi-vendor interoperability); assessment and presentation of the structure of virtualized and centralized systems from different vendors, with particular attention to the ability to operate within the virtual environment used by the operator (e.g. VMware or similar). Scenarios for solution upgrade (“hardware refresh”) shall be defined for a period of at least 5 years.

    - Evaluation of testing methods for the solution and the equipment required for testing both during deployment and during operation of the technical solution. The Hardware-in-the-Loop (HIL) testing concept and integration of a digital twin shall be included.

    - Definition of cybersecurity requirements for the solution, identification of applicable IEC standards governing cybersecurity and the equipment compliant with them. The analysis shall include recommendations derived from EU directives; requirements for cybersecurity resilience testing shall be defined; and the need for security certification shall be evaluated.

    - Synchronization of processes using the PTP (IEEE 1588 v2) protocol. Selection of the synchronization topology, evaluation of the required resilience to GNSS interference and disruptions, and provision of recommendations for mitigation measures. A multi-GNSS source architecture (GPS, Galileo, GOVSATCOM, IRIS²) shall be considered, and a methodology for measuring time deviation (TE/MTIE/TDEV) shall be included.

    - Identification of tools for analysing processes and data exchange that allow: operational analysis of disturbances and system performance from different perspectives; definition of requirements for automatic event detection algorithms and AI-based anomaly detection; integration with incident management systems; and implementation of traceability and data audit requirements.

    - Evaluation of existing and proposal of new data network and cybersecurity solutions, data exchange mechanisms and protocols used with SCADA/EMS and IT systems, as well as the availability requirements of data exchange and centralized systems and the measures required to ensure such availability.

    - Provision of solutions for teleinformation collection and transmission (RTU) integrated into the centralized system, including analysis and recommendations for maintenance (operation), taking into account the functions of the centralized system and its software layers.

## Structure of the study and reporting stages

The scope of the study is divided into three separate parts, which are considered independent stages (KPIs) with separate interim results:

  - Legal and organisational aspects.

  - Protection and Automation (PA) technical aspects.

  - IT/OT technical aspects.

The Contractor shall submit the interim results (reports) for each stage and present them to the Contracting Authority. Each stage shall be considered completed only after written approval by the Contracting Authority. During the study, the Contractor shall prepare and submit the following documents:

    - Interim Report No. 1: Legal and organisational aspects.

    - Interim Report No. 2: PA technical aspects.

    - Interim Report No. 3: IT/OT technical aspects.

    - Final integrated report (combining all parts).

  - The Contractor shall submit the documents in Lithuanian or English (to be agreed with the Contracting Authority).

  - Reports shall be submitted in an editable format (MS Word or PowerPoint).

  - Substation solution architecture diagrams shall be submitted in editable .dwg format.

## General requirements

The Contractor shall ensure that the results of the study are practical, implementable and applicable within the context of the transmission network operated by the Contracting Authority, and that the recommendations provided are based on standards, market solution analysis and technical evaluation.

The Contractor shall:

  - Provide a clear study methodology (workflow, information collection, analysis methods, interim presentations).

  - Evaluate all solutions in the context of 110–400 kV substations, taking into account the reliability requirements of critical infrastructure.

  - Provide justification for the recommendations, indicating assumptions, limitations and technical arguments.

  - Identify applicable standards and provide their interpretation, rather than only listing the standards.

- Project coordination and communication

The Contractor shall ensure project management and communication with the Contracting Authority, including:A kick-off meeting within 10 working days after the contract enters into force.

  - Progress review meetings held at least once per month.

  - Presentations of interim results at the end of each stage.

  - A final presentation of the study at the Contracting Authority’s office or remotely.

  - Meeting minutes provided electronically within 2 working days after each meeting.

- Preliminary project schedule

The total duration for the preparation of the study shall not exceed 12 (twelve) months from the date of entry into force of the contract.The preliminary schedule is provided for planning purposes. The final timeline shall be agreed with the selected Contractor.

| Stage | Duration (months) | Ke |
| --- | --- | --- |
| Stage 1: Legal and organizational issues | 1–4 | Interim report No. 1 |
| Stage 2: RAA technical issues | 3–8 | Interim report No. 2 + architecture model |
| Stage 3: IT/OT technical issues | 6–11 | Interim report No.3 |
| Integration and final report | 11–12 | Final consolidated report |

- Requirements for the supplier’s team

The minimum requirements for the project team are specified in Annex 4 of the procurement documentation  – “Qualification Requirements”. The Supplier must appoint:

  - Project coordinator

  - PA/substation automation expert or team of experts.

  - IT/OT infrastructure/telecommunications expert or team of experts.

- Confidentiality and data protection

The Supplier must ensure the confidentiality of the information received and use it solely for the purposes of this study. Technical data and diagrams provided by the Contracting Authority may not be shared with third parties without the written consent of the Contracting Authority.

- Annexes

Annex 1 - Glossary of Terms

Annex 2 - Substation technical information

Annex No.1 – Glossary of terms

| Term | Definition |
| --- | --- |
| Solution | The study examines the entirety of the centralized and virtualized PA system, including hardware, software, communication infrastructure, time synchronization, cybersecurity measures, and operational processes. |
| PA (Protection and Automation) | A set of technical and software functions intended to protect electrical network equipment from faults and to manage automatic operating modes. |
| Bay | A functional element of a substation (e.g., line, transformer, shunt reactor bay) with its own primary devices and assigned control, measurement, protection, and automation functions. |
| Centralization | A PA architecture principle in which protection and automation functions for multiple substation bays are executed on one or several common computing devices (e.g., servers), rather than separate physical IEDs for each bay. |
| Virtualization | A technical solution in which PA functions and their execution environment are implemented as software components (virtual machines or containers) on a shared server platform, ensuring isolated operation and managed resource allocation. |
| Digitization | The process of converting analog measurement and control signals in the substation into digital form and transmitting them via standardized protocols (e.g., IEC 61850 GOOSE/Sampled Values), enabling automated data processing and system integration. |
| IED (Intelligent Electronic Device) | A microprocessor-based device performing one or more protection, automation, measurement, or control functions, typically supporting IEC 61850 communication. |
| Decentralized PA architecture | A solution where each bay uses separate physical PA devices (IEDs) with local protection and automation functions. |
| IEC 61850 | An international standard defining the communication model, data structures, and protocols for digital substations (e.g., MMS, GOOSE, Sampled Values). |
| Station Bus | An IEC 61850 communication layer for data exchange between substation control/protection devices (e.g., IED, HMI, SCADA gateway), typically using MMS and GOOSE. |
| Process Bus | An IEC 61850 communication layer for real-time transmission of measurement and control signals from primary equipment (e.g., Merging Unit) to protection functions, typically using Sampled Values and GOOSE. |
| IEC 60255 | A set of international standards defining functional, testing, and operational requirements for protection devices. |
| IEC 60834-1 | Standard defining dependability/security principles and evaluation methodology for protection systems. |
| IEC 61869-13 | Standard specifying requirements and data interfaces for digital instrument transformers (Digital Interface). |
| Merging Unit (MU) | A device that collects analog measurement signals (current/voltage) and transmits them digitally (Sampled Values) to the process network. |
| Multi-vendor interoperability | The ability of devices and software from different manufacturers to operate together via standardized interfaces and protocols (e.g., IEC 61850). |
| OT (Operational Technology) | The domain encompassing physical process control systems in energy facilities (PA, SCADA, RTU, telecommunications). |
| IT/OT integration | Solutions where OT infrastructure is connected to IT management, security, analytics, and data systems while maintaining segmentation and cybersecurity principles. |
| GNSS | Global navigation satellite systems (e.g., GPS, Galileo) used as precise time sources in substations. |
| HIL (Hardware-in-the-Loop) | A testing method where real equipment (e.g., protection functions or IEDs) is tested with a simulated electrical system in real time. |
| Digital Twin | A virtual model of a substation or system used for testing, analysis, configuration validation, and evaluation of operational scenarios. |
| Hardware refresh | Planned update/replacement of server or network equipment, maintaining system functionality and compatibility. |
| Sensitivity analysis | An economic evaluation method modeling how the result changes with variation of key assumptions (inflation, equipment costs, refresh cycles). |
| Traceability | A requirement that all configuration changes, events, and actions are logged and can be audited. |
| Audit trail | A technical record ensuring that system actions, logins, and configuration changes are documented and verifiable. |

Annex No. 2 – Substation technical information

This annex provides information about the substation electrical diagram. The information is intended for potential suppliers to help them understand the scope of the project. Suppliers are encouraged to use this information when preparing their proposals and, if necessary, request clarifications regarding specific technical solutions. The full substation diagram will be provided to the winning supplier.

Substation voltage levels: 330 kV / 110 kV / 10 kV

Bays:

- 330 kV:

  - 4 connections (transmission lines) + 2 spare

  - 2 autotransformers 330/110 kV

- 110 kV:

  - 2 connections (transmission lines) + 1 spare

  - 2 connections to 10 kV auxiliary transformer

Switchgear type: Open-air switchgear.