## Generator
LIST OF SERVICE ACTIVITIES GENERATOR | Inspection |  |  | Report
Specification of activities | A | B | C
SIEMENS GENERATOR
Dismantling
Dismantle the generator panels |  | X | X | N
Open the bearing and coupling covers |  | X | X | N
Measure bearing clearances, contact pattern, and play |  | X | X | R
Check for proper operation |  |  | X | R
Measure bearing base insulation |  | X | X | R
Generator maintenance equipment
Check the condition and operation of temperature gauges and alarms* |  | X | X | R
Replacement of grounding brushes. | X | X | X | R
Check the operation of anti-condensation heaters* |  | X | X | R
Rotor (electrical measurements)
Measure insulation resistance |  | X | X | R
Measure winding resistance |  |  | X | R
Rotor (visual inspection)
Inspect bearing shafts |  | X | X | R
Inspect sealing surfaces |  | X | X | R
Inspect support rings (visually) |  |  | X | R
Inspect fans (visually) |  | X | X | R
Inspect balancing weights (visually) |  | X | X | R
Inspect end windings (visually) |  | X | X | R
Perform endoscopic inspection of end windings, particularly inspecting the DC rotor shaft current conductor and A coil contacts |  |  | X | R
Perform endoscopic inspection of the air gap between the rotor and stator windings |  |  | X | R
Perform endoscopic inspection of the angular soldered joint at the transition of the pole transition conductor from pole 1 to pole 2 |  |  | X | R
Stator (electrical measurements)
Monitor component temperatures | X | X | X | R
Monitor cooling air temperature | X | X | X | R
Measure stator winding insulation resistance |  | X | X | R
Measure temperature sensor insulation resistance |  | X | X | R
Measure winding resistance |  |  | X | R
Measure temperature sensor resistances |  |  | X | R
High-voltage testing |  |  | X | P
tan δ measurement and partial discharge measurements |  |  | X | P
Partial discharge |  |  | X | P
Stator (visual inspections)
Inspect end winding spacers |  | X | X | R
Inspect phase ring and phase ring supports |  | X | X | R
Inspect pressure plates and their securing elements |  | X | X | R
Inspect end winding supports and their reinforcement |  | X | X | R
Check the position and quick fastening of the external GRP ring |  | X | X | R
Check the position and quick fastening of the internal GRP ring |  | X | X | R
Check the firm attachment of the internal GRP ring segments |  | X | X | R
Inspect end winding insulation |  | X | X | R
Check surface sealing |  | X | X | R
Inspection of end winding leads |  | X | X | R
Inspection of main terminal screw connections |  | X | X | R
Inspection of cable insulation |  | X | X | R
Inspection of resistance thermometer connections |  | X | X | R
Sealing check between the laminated core and air guide walls or between the air guide walls and housing, and if necessary, between the laminated core and housing |  |  | X | R
Replacement of shaft grounding carbon brushes. | X | X | X | R
Inspection of the measuring circuit slip ring surface |  | X | X | R
Bearings
Monitoring of lubrication device operation* | X |  |  | R
Monitoring of bearing temperature | X |  |  | R
Removal of oil mist condensate | X |  |  | R
Inspection of bearing insulation and renewal if necessary |  | X | X | R
Inspection of white metal contact and adhesion in bearings |  | X | X | R
Inspection of bearing clearances |  | X | X | R
Inspection of bearing housing seating in the bearing housing support |  | X | X | R
Inspection of multilayer sealing rings and renewal of sealing strips if necessary |  | X | X | R
Inspection of bearing thermometer |  | X | X | R
Inspection of hydraulic shaft lift |  | X | X | R
Cooler
Inspection of the air filter in the cooler cover for contamination | X |  | X | R
Inspection of cooling water inlet and outlet openings |  | X | X | R
Inspection of ventilation and drainage pipes |  | X | X | R
Pressure test |  |  | X | R
Opening of cooler return chamber, inspection of coating, installation of new seals |  |  | X | R
Excitation system (electrical measurements)
Inspection of winding insulation resistances |  | X | X | R
Inspection of diode blocking characteristics |  | X | X | R
Inspection of RC circuit blocks and/or overvoltage protection |  |  | X | R
Excitation system (visual inspections)
Inspection of the condition and operation of rotating rectifier wheels, inspection of stator and rotor windings |  | X | X | R
Reassembly
Measurement of bearing clearances and looseness |  | X | X | N
Covering and sealing of bearings, readjustment of oil scraper |  | X | X | N
Assembly of generator panels |  | X | X | N
Installation of the generator |  |  | X | N
Visual inspection of the Line side and Neutral Point
Internal condition inspection, cleaning of dust and deposits | X | X | X | R
Check the cubicles for damages, worn sealings at the flaps | X | X | X | R
Inspection of grounding connections. The contact transition resistance must be ≤0.05 Ω. Repair if necessary. | X | X | X | R
Check the screwed connections for the signs of loosening's, overheating or discoloration. Tighten and clean contacts if necessary. | X | X | X | R
Check the current and voltage transformers, neutral point transformer, resistors, and other components for visual damage, such as cracks in the casing | X | X | X | R
Inspection of surge protection capacitors – checking for oil leakage or other damage. | X | X | X | R
Explanations:
N - report is not required
R - report is required
*If the condition of the device is poor or the device is faulty – replace it.