BATERIJŲ ENERGIJOS KAUPIMO SISTEMOS TECHNINĖ PRIEŽIŪRA/

BATTERY ENERGY STORAGE SYSTEM MAINTENANCE

| TECHNINĖ SPECIFIKACIJA |  | TECHNICAL SPECIFICATION |
| --- | --- | --- |
| 1. | Baterijų energijos kaupimo sistema (toliau – BEKS), kurią sudaro BEKS kubas (toliau – Kubas) ir BEKS valdymo sistema (toliau – BEKS VS). BEKS talpa - 1MW/1MWh. Kubas yra atskiras energijos kaupimo įrenginys, kuriame yra baterijos, baterijų valdymo sistema, duomenų gavimo sistema ir kita įranga bei priedai būtini užtikrinti jos ilgalaikį veikimą lauko sąlygomis. BEKS VS sudaro: serveriai, TSPĮ (RTAC), telekomunikacijų įranga, valdikliai, žmogus-mašina sąsaja (HMI) maitinimo ir kita infrastruktūros įranga. | Battery energy storage system (further - BESS) which is concluded of BESS cube (further - The Cube) and BESS control system (further - BEES CS). BESS Size - 1MW/1MWh. BESS Cube is a discrete energy-storage unit that includes batteries and battery management system, consisting of servers, TRAC, telecommunication equipment, controllers, HMI, power supply and other equipment and accessories necessary to maintain health and long-term operation in an outdoor environment. BESS CS concluded of: servers, RTAC, telecommunication equipment, controllers, HMI, power supply and other equipment. |

Nuotrauka Nr. 1  Kubas, vaizdas iš priekio. Aukštis ~2.6 metro./

Photo No. 1. The Cube, front view. Height ~2.6 meters.

| 2. | Kubo pagrindinės charakteristikos/ |  | Basic characteristics of the Cube |
| --- | --- | --- | --- |
| 2.1. | Matmenys (A x P x D)/ Dimensions (H x W x D): |  |  |
| 2.1.1. | 2 549 x 2 578 x 2 160 mm |  |  |
| 2.1.2. | 2 549 x 2 578 x 2 257 mm |  |  |
| 2.2. | Svoris (iš viso) kg/ Cube Weight (in total) kg: |  |  |
| 2.2.1. | 8.200 ± 2% |  |  |
| 2.2.2. | 8.550 ± 2% |  |  |
| 2.3. | Korpusas/ Enclosure: | NEMA 3R tipas/ NEMA Type 3R |  |
| 2.4. | IP reitingas/ IP Rating: | IP55 |  |
| 2.5. | Akumuliatoriaus aušinimas/ Battery Cooling: | skysčiu/liquid |  |
| 2.6. | Baterijos/ Battery: | Ličio jonų sandarios celės/Lithium ion sealed cells |  |
| 2.7. | Serijinis Numeris/ Serial Number | F010-2114-0146-06010003-16-2.2, F010-2114-0147-06010003-08-2.2 |  |

| 3. | Reikalavimai aptarnavimui | Requirements for maintenance |
| --- | --- | --- |
| 3.1. | BEKS paleidimas po ilgalaikio nenaudojimo. Prieš paleidimą turi būti atliekama detali įrenginio apžiūra ir patikrinimas pagal gamintojo reikalavimus, nustatomi ir pašalinami defektai. Vykdant BEKS veikimo patikrinimą turi būti atliekamas visų sistemų patikrinimas, tame tarpe ir varžtų užveržimo patikrinimą, pagrindinių elementų termoviziją, duomenų perdavimo įrenginių priežiūrą, aukštos įtampos įrenginių ir gaisro gesinimo sistemos patikrinimus. | BESS start-up after a long-term non-use. Before start-up, a detailed inspection and check of the BESS and BESS CS must be carried out in accordance with the manufacturer's requirements, defects must be identified and removed. The verification of the operation of the BESS shall include a proper inspection of all systems, including inspection of bolt tightening, thermovision of the main elements, maintenance of data transmission equipment, inspections of high voltage equipment and fire extinguishing system. |
| 3.2. | Nuotolinė konsultacija. Paslauga užsakoma pagal poreikį. Vykdoma telefonu ar vaizdo ryšiu. Nustatomi ir pašalinami gedimai nuotoliniu būdu. Atliekamas programinės įrangos atnaujinimas pagal gamintojo rekomendacijas. Konsultuojami BEKS priežiūrą atliekantys Litgrid AB darbuotojai. Konsultacija atliekama nustačius BEKS veikimo sutrikimą ar kitais BEKS priežiūros klausimais vykdant BEKS eksploataciją. | Remote consultation. The service will be ordered as needed. It is performed by telephone or video call. Faults are identified and eliminated remotely. Software updates are performed according to the manufacturer's recommendations. Litgrid AB employees performing BESS maintenance are consulted. Consultation is performed when a BESS malfunction is detected or other BESS maintenance issues are addressed during BESS operation. |
| 3.3. | Konsultacija pastotėje. Paslauga užsakoma nustačius poreikį po nuotolinės konsultacijos. Reikalingas darbuotojo atvykimas į pastotę. Turi būti atliekamas smulkių defektų šalinimas, BEKS paleidimas po atsijungimo. Medžiagos į darbų kainą neįtrauktos. | Consultation at the substation. The service is ordered after determining the need after remote consultation. An employee's arrival at the substation is required. Minor defects must be eliminated, BESS is started after disconnection. Materials are not included in the price of the work. |
| 4. | Tiekėjo įsipareigojimai/ Supplier 's obligation |  |
| 4.1. | BEKS paleidimo po ilgalaikio nenaudojimo paslauga atliekama po sutarties pasirašymo per 2 savaites. Vėliau, esant paslaugos poreikiui, paslaugos suteikimo terminas suderinamas tarpusavyje, bet ne vėliau kaip per 1 mėnesį nuo paslaugos užsakymo. | The service of start-up the BESS after a long-term non-use is performed within 2 weeks after signing the contract. Later, if there is a need for the service, the term for providing the service is mutually agreed upon, but no later than 1 month from ordering the service. |
| 4.2. | Nuotolinei konsultacijai turi būti pateikti atsakingo darbuotojo kontaktai, kuriais atsakymo pateikimo terminas – 24 val. | For remote consultation, the contact details of the responsible employee must be provided, with a response time of 24 hours. |
| 4.3. | Konsultacijos pastotėje suteikimo terminas - 14 kalendorinių dienų arba kitas tarpusavyje suderintas terminas. | The response time for consultations at the substation is 14 calendar days or another mutually agreed time. |
| 4.4. | Tiekėjas prisijungimą prie BEKS VS turi gauti iš gamintojo Fluence | The supplier must obtain a connection to BESS CS from the manufacturer Fluence. |