REGARDING THE RESPONSES TO SUPPLIERS' QUESTIONS

We are sending responses to suppliers questions in an ongoing procurement of (2025-IGN-184) Battery Energy Storage System (BESS) and maintenance services during their operation.

To avoid interpretations of the content, we quote the questions of the suppliers exactly as they were submitted via the Central Procurement Information System (hereinafter - CPP IS) (text is not edited).

- Question: Clause 3.4 of the Technical Specification. Power Conversion System to be integrated internally. Having separated PCS and Battery containers will increase the solution flexibility. Please consider separate solution.

- Answer: Clause 3.4 of the Technical Specification, as defined in Table No. 3 under the section “Power Conversion System”, clearly requires that the PCS shall be integrated internally. This means the PCS must be part of the BESS enclosure and cannot be installed as a separate container or skid. Therefore, only solutions with an internally integrated PCS are considered compliant. Any solution with separated PCS and battery containers would be treated as a deviation.

- Question: Clause 4 of the Technical Specification. Back up Power. Is the back up power for uninterruptible power supply and seamless switching for one of the connection points?

2.  Answer: According to Clause 4 of the Technical Specification and the “Backup power” section of Table No. 3, the backup power system is intended to provide uninterruptible and seamless power supply, not only auxiliary or emergency power. The requirements include backup mode operation, an integrated or compatible Automatic Transfer Switch (ATS), configurable critical load prioritization, island‑mode operation, and a reconnection time of ≤ 20 ms, indicating near‑seamless switching capability.

Procurement Project Manager Alina Dralo, phone no. +370 620 93298