TECHNINĖ SPECIFIKACIJA

GAMTINIŲ DUJŲ (METANO) NUOTĖKIŲ MATAVIMO, DUOMENŲ ANALIZĖS IR ATASKAITŲ PARENGIMO PASLAUGŲ PIRKIMAS

- SĄVOKOS IR SUTRUMPINIMAI

Pirkėjas – AB „Amber Grid“. Daugiau informacijos apie Pirkėją ir jo veiklą galima rasti www.ambergrid.lt

Paslaugos teikėjas – ūkio subjektas – fizinis asmuo, privatusis juridinis asmuo, viešasis juridinis asmuo, kitos organizacijos ir jų padaliniai ar tokių asmenų grupė, su kuriuo Pirkėjas sudaro Sutartį;

Paslaugos – gamtinių dujų (metano) nuotėkių matavimo, duomenų analizės ir ataskaitų parengimo paslaugos.

Sutartis – sutartis, sudaroma tarp Paslaugos teikėjo ir Pirkėjo dėl gamtinių dujų (metano) nuotėkių matavimo, duomenų analizės ir ataskaitų parengimo paslaugų;

Reglamentas – 2024 m. birželio 13 d. Europos Parlamento ir Tarybos reglamentas Nr. 2024/1787 dėl energetikos sektoriuje išmetamo metano kiekio mažinimo, kuriuo iš dalies keičiamas reglamentas (ES) 2019/942 (nuoroda – Regulation - EU - 2024/1787 - EN - EUR-Lex);

Neeilinis iškvietimas – tai skubus, neeilinis iškvietimas vykdyti metano nuotėkių matavimus.

Sutrumpinimai:

EPA 21 – Jungtinių Amerikos Valstijų Aplinkos apsaugos agentūros patvirtinta testavimo metodika (angl. Environmental Protection Agency EPA Method 21);

LST EN 15446:2008 – Lietuvos standartas atitinkantis Europos standartą EN 15446:2008;

ES – Europos Sąjunga;

OGMP 2.0 – The Oil & Gas Methane Partnership 2.0 (nuoroda – Resources | The Oil & Gas Methane Partnership 2.0);

JDKS – Jauniūnų dujų kompresorių stotis;

PDKS – Panevėžio dujų kompresorių stotis;

DSS – Dujų skirstymo stotis;

DAS – Dujų apskaitos stotis;

DASRS – Dujų apskaitos ir slėgio reguliavimo stotis;

DSRM – Dujų slėgio ribojimo mazgai;

ČA – Uždarymo įtaisų aikštelė;

ppm – Koncentracijos matavimo vienetas (angl. parts per million).

- PIRKIMO OBJEKTAS

  - Pirkimo objektas – gamtinių dujų (metano) nuotėkių matavimo, duomenų analizės ir ataskaitų parengimo paslaugos (toliau – Paslaugos).

  - Pirkimo objektas į dalis neskaidomas. Paslaugų teikėjas turės siūlyti visą Pirkimo objekto kiekį/apimtį.

  - Pirkimo objektas apima šias paslaugas:

    - kontaktinių šaltinio lygmens ir objekto lygmens metano nuotėkių matavimo Pirkėjo fiziniuose objektuose paslaugos;

    - matavimo duomenų analizės ir ataskaitų parengimo Paslaugos.

  - Pirkėjas siekia įsigyti Paslaugas, kurių techniniai reikalavimai aprašyti šioje Techninėje specifikacijoje, ketinamoje sudaryti Sutartyje ir pirkimo dokumentuose nustatytuose parametruose bei sąlygomis.

- PIRKIMO APIMTYS IR CHARAKTERISTIKA

  - Preliminarios matuojamų objektų apimtys:

    - Jauniūnų dujų kompresorių stotis*;

    - Panevėžio dujų kompresorių stotis*;

    - Dujų skirstymo stotys*;

    - Dujų apskaitos stotys*;

    - Dujų apskaitos ir slėgio reguliavimo stotis*;

    - Dujų slėgio ribojimo mazgai*;

    - Uždarymo įtaisų aikštelės*.

Preliminarios matavimo taškų (potencialių gamtinių dujų (metano) nuotėkių šaltinių) apimtys objektuose nurodytos 1 lentelėje.

1 lentelė. Preliminarus matavimo taškų skaičius fiziniuose objektuose.

| Nr. | Objektas* | Preliminarus matavimo taškų skaičius** | Pastabos |
| --- | --- | --- | --- |
| 1. | Jauniūnų dujų kompresorių stotis (JDKS) | 10 000 | Matavimai turi būti atliekami atsižvelgiant į kompresorių darbo režimą. |
| 2. | Panevėžio dujų kompresorių stotis (PDKS) (kartu su Piniavos DSS) | 3 500 | Matavimai turi būti atliekami atsižvelgiant į kompresorių darbo režimą. |
| 3. | Dujų skirstymo stotys (DSS) – 64 vnt. Dujų apskaitos stotys (DAS) – 3 (Kiemėnai, Šakiai, Mažeikiai) Dujų apskaitos ir slėgio reguliavimo stotis (DASRS) (Santaka) Dujų slėgio ribojimo mazgai (DSRM) – 4 (Dauparai, Lapkasiai, Vilnius, Marijampolė) | 63 500 | - |
| 4. | Uždarymo įtaisų aikštelės (ČA) – 318 vnt. | 64 000 | - |
| Viso: |  | 141 000 |  |

Pastabos:

*Detalus vietų sąrašas bus pateikiamas Paslaugos teikėjui Sutarties vykdymo metu po Sutarties pasirašymo.

**1 lentelėje pateikti preliminarūs matavimo taškų skaičiai objektuose.

- REIKALAVIMAI PIRKIMO OBJEKTUI

  - Kontaktiniai šaltinio lygmens ir objekto lygmens (angl. site level) gamtinių dujų (metano) nuotėkių matavimai turi būti vykdomi taikant EN 15446 standarto (arba lygiaverčio) standarto reikalavimus bei vadovaujantis 2024 m. birželio 13 d. Europos Parlamento ir Tarybos reglamentas Nr. 2024/1787 dėl energetikos sektoriuje išmetamo metano kiekio mažinimo, kuriuo iš dalies keičiamas reglamentas (ES) 2019/942 (toliau – Reglamentas) ir atsižvelgiant į The Oil & Gas Methane Partnership 2.0 (toliau – OGMP 2.0) rekomendacines gaires.

  - Kontaktiniai šaltinio lygmens metano nuotėkių matavimai Pirkėjo fiziniuose objektuose.

    - Paslaugos teikėjas, naudodamas kontaktinių matavimų (2 tipo, angl. type 2) geriausią esamą metodiką (taikant EPA21 ar LST EN 15446:2008 ar lygiavertę) ir rinkoje prieinamas geriausias matavimo priemones, turi išmatuoti potencialias metano nuotėkio vietas, atsižvelgiant į OGMP 2.0 gairėse pateikiamas rekomendacijas bei į Reglamente nustatytus reikalavimus.

    - Matavimams naudojamos matavimo priemonės turi atitikti Reglamento reikalavimus (aktuali redakcija su vėlesniais pakeitimais).

    - Matavimai turi būti atlikti tiesioginiu (kontaktiniu) būdu (2 tipo, angl. type 2), naudojant sukalibruotą įrangą, kurios minimali aptikimo riba ne daugiau kaip 1 ppm (pvz. FID arba PID arba TDLAS arba lygiavertė veikimo technologija), kuri tiesiogiai fiksuotų metano koncentraciją ppm (angl. parts per million).

    - Jeigu matavimo taškas negali būti patikrintas tiesiogiai, nes yra sunkiai pasiekiamas ir dėl to kyla pavojus darbuotojų saugumui, Paslaugų teikėjas turi rinktis matavimo priemones taip, kaip numato Reglamentas (aktuali redakcija su vėlesniais pakeitimais) ir matavimus atlikti naudojantis kitomis priemonėmis (pvz. OGI arba lygiavertės technologijos).

    - Paslaugos teikėjas, pasitelkdamas savo turimą įrangą ir resursus, pagal suderintą darbų grafiką, privalo patikrinti potencialius metano nuotėkio šaltinių taškus, kurie detaliau nurodyti šios techninės specifikacijos 1 lentelėje. Matavimų rezultatų duomenis priskirti atitinkamiems inventoriaus hierarchijos objektams.

    - Paslaugos teikėjas matavimo metu turi fiziškai pažymėti violetinės spalvos etikete įrenginių komponentus, kur nustatomi metano nutekėjimai, nepriklauso nuo jų dydžio.

    - Paslaugos teikėjas turi nufotografuoti užfiksuotas ir pažymėtas aptiktas vietas, kuriose nustatytas metano nuotėkis. Nuotraukoje turi būti tiksliai nurodyta nuotėkio vieta.

    - Paslaugos teikėjas identifikavęs fizinių metano nuotėkio matavimo taškų ir technologinės schemos neatitikimus, informuoja Pirkėją ne vėliau kaip per 5 (penkias) kalendorines dienas ir el. paštu pateikia schemą su pažymėtomis neatiktimis Pirkėjui.

    - Paslaugos teikėjas fizinių matavimų vykdymo metu turi kas savaitę Pirkėjui teikti aptiktų dujų nuotėkių informaciją ir matavimų vykdymo statusą. Paslaugos Teikėjas teikdamas informaciją turi nurodyti išmatuotą nuotėkio dydį ppm, visiems aptiktiems dujų nuotėkiams nepriklausomai nuo jų dydžio, objekto identifikacinį kodą ir matavimo taško identifikacinį kodą pagal turto hierarchijos duomenis, nuotėkio vietos nuotrauką, matavimo datą ir laiką, matavimo prietaisą, matavimus atlikusio operatoriaus informaciją. Pateikiamos informacijos duomenų šablonas nurodytas šios techninės specifikacijos 2 lentelėje.

    - Paslaugos teikėjas turi identifikuoti, kurie aptikti pratekėjimai yra susiję su technologinio proceso išleidimais (IŠLEIDIMAS, angl. VENT), o kurie kyla dėl komponentų nesandarumo ar netinkamo veikimo (NUOTĖKIS, angl. LEAK).

    - Paslaugos teikėjo darbuotojai bus lydimi į Pirkėjo objektus vykdyti matavimų suderinus su Pirkėjo atsakingais asmenimis, ne vėliau kaip prieš 14 (keturiolika) kalendorinių dienų. Matavimų metu Pirkėjo atsakingi asmenys gali vykdyti aptiktų dujų nuotėkių remonto darbus. Tokiu atveju Paslaugos teikėjas tą pačią ar kitą darbo dieną turi atlikti pakartotinį matavimą po remonto. Tiek pirmo matavimo, tiek remonto ir pakartotinio matavimo duomenis Paslaugos teikėjas privalo detaliai užfiksuoti ataskaitose. Paslaugų teikėjas turės vadovautis Pirkėjo nustatyta sutikimo dirbti suteikimo tvarka, nuoroda pateikiama čia: Sutikimo dirbti suteikimo tvarka.

    - Pirkėjas gali užsakyti Paslaugos tiekėjo matavimų Paslaugas neeiliniam, skubiam metano nuotėkių matavimui (toliau – Neeilinis iškvietimas). Esant poreikiui vykdyti Neeilinį iškvietimą metano nuotėkių matavimui, Pirkėjas teikia užsakymą el. paštu Paslaugos tiekėjui nurodydamas matavimų poreikio apimtį. Paslaugos tiekėjo darbuotojas turi atvykti atlikti matavimų ne vėliau kaip per 14 kalendorinių dienų nuo Neeilinio iškvietimo užsakymo pateikimo dienos. Paslaugos tiekėjas į Neeilinio iškvietimo standartinį įkainį įtraukia visas aktualias išlaidas (komandiruotės kaštai, transportas, skrydžių bilietai ar kt.). Esant Neeiliniam iškvietimui už atliktus metano nuotėkio matavimo darbus su Paslaugos tiekėju atsiskaitoma pagal pateiktus standartinius įkainius (kaip nurodyta 3 priedo 1 arba 4 arba 5 punktuose) bei pridedant Neeilinio iškvietimo standartinį įkainį (kaip nurodyta 3 priedo 2 punkte).

    - Matavimo informacijos duomenų pateikimo šabloninė lentelė, pateikta šios techninės specifikacijos 2 lentelėje, gali būti derinama ir koreguojama, papildomi ar patikslinami laukai, Paslaugos teikėjui patikslinimus ir pakeitimus suderinus tu Pirkėju.

2 lentelė. Duomenų pateikimo formos šablonas.

| Objekto ID | Pildoma visiems matavimo taškams |
| --- | --- |
| Matavimo taško ID | Pildoma visiems matavimo taškams |
| Matavimo rezultatas | Pildoma visiems matavimo taškams |
| Matavimo rezultato matavimo vienetas | Pildoma visiems matavimo taškams |
| Matavimo data | Pildoma visiems matavimo taškams |
| Matavimo laikas | Pildoma visiems matavimo taškams |
| Matavimą atliko | Pildoma visiems matavimo taškams |
| Matavimo prietaisas | Pildoma visiems matavimo taškams |
| Nuotėkio reikšmingumas | Pildoma tik užfiksavus dujų nuotėkį (remontuojamas ar stebimas) |
| Nuotėkio tipas | Pildoma tik užfiksavus dujų nuotėkį (išleidimas ar nuotėkis) |
| Nuotėkio vietos detalus aprašymas | Pildoma tik užfiksavus dujų nuotėkį, jeigu aktualu |
| Remontas atliktas iškart | Pildoma visiems matavimo taškams |
| Matavimo rezultatas po remonto | Pildoma tik remontuotiems taškams |
| Matavimo rezultato matavimo vienetas po remonto | Pildoma tik remontuotiems taškams |
| Matavimo data | Pildoma tik remontuotiems taškams |
| Matavimo laikas | Pildoma tik remontuotiems taškams |
| Matavimą atliko | Pildoma tik remontuotiems taškams |
| Matavimo prietaisas | Pildoma tik remontuotiems taškams |

  - Objekto lygmens metano nuotėkių matavimai Pirkėjo fiziniuose objektuose.

    - Paslaugos teikėjas, naudodamas objekto lygmens (angl. site level)  matavimų geriausią esamą metodiką, turi išmatuoti Pirkėjo objektus naudodamasis savo turima ir (arba) išsinuomota įranga, atsižvelgiant į OGMP 2.0 gairėse pateikiamas rekomendacijas bei į Reglamente nustatytus reikalavimus.

    - Matavimams naudojamos matavimo priemonės turi atitikti Reglamento reikalavimus (aktuali redakcija su vėlesniais pakeitimais).

    - Objekto lygmens (angl. site level)  metano nuotėkių matavimai turi būti vykdomi tuo pačiu metu kaip ir kontaktiniai šaltinio lygmens metano nuotėkių matavimai, siekiant kuo tikslesnio duomenų sulyginimo.

    - Paslaugos teikėjas turi atsižvelgti į oro sąlygas, kad matavimai būtų atliekami tik esant saugioms ir optimalioms sąlygoms ir vadovaujantis matavimo prietaisų gamintojų instrukcijomis.

    - Paslaugos teikėjas turi įsivertinti ir pasirinkti tinkamiausią matavimo įrangą atsižvelgdamas į Pirkėjo skirtingų objektų charakteristikas.

    - Uždarymo įtaisų aikštelės yra įrengtos atvirose lauko erdvėse, DKS, DSS, DAS, DASRS, DSRM objektai įrengti uždarose patalpose, tačiau turi ir atviroje lauko erdvėje esančių įrenginių su potencialiais metano nuotėkio šaltiniais. Iš 65 dujų skirstymo stočių, 35 yra įrengtos konteineriuose, kita dalis įrengta didesnio tipo konteineriuose arba pastatuose. Metano nuotėkio matavimo taškų fiziniuose objektuose detalesnė informacija pateikta šios techninės specifikacijos 1 Priede.

    - Paslaugos teikėjas turi užtikrinti, kad vykdant objekto lygmens matavimus fiziniuose objektuose, būtų išmatuoti visi objekte esantys potencialūs metano nuotėkio šaltiniai ir nepilno sudeginimo emisijų šaltiniai – dujas deginančių katilų emisijos.

  - Atliktų matavimų ataskaitų parengimas ir pateikimas.

    - Kontaktinių šaltinio lygmens matavimų ataskaitos parengimas ir pateikimas.

      - Paslaugos teikėjas privalo atlikti matavimų analizę ir parengti matavimų ataskaitos šabloną. Ataskaitoje turi būti nurodytos pamatuotų vietų (taškų) kiekybinės praleidimų reikšmės per laiko vienetą (g/val.) ir koncentracijos matavimų vertės (ppm), objekto identifikacinį kodą ir matavimo taško identifikacinį kodą pagal turto hierarchijos duomenis, matavimo data ir laikas, matavimo prietaisas, matavimus atlikusio operatoriaus informacija, vietos informacija, vamzdyno ar kito įrengimo technologinis numeris, diametras, terpė, taško vieta, pateikiant nuorodą į technologines schemas, susietas su hierarchija. Ataskaitos šabloną raštu suderinti su Pirkėju prieš pradedant vykdyti fizinius matavimus objektuose. Ataskaita turi būti pateikta ne vėliau kaip per 20 (dvidešimt) kalendorinių dienų po kontaktinių šaltinio lygmens matavimų įvykdymo.

      - Jeigu Paslaugos teikėjas rengdamas ataskaitą atliko matavimo vienetų perskaičiavimus, tokiu atveju turi pateikti perskaičiavimo metodiką, kuri turi atitikti galiojančius tarptautinius standartus, su detaliu paaiškinimu, neapibrėžtimis, koeficientais (jei tokie naudojami perskaičiavime) bei skaičiavimo paklaidomis, kad būtų išvengta srauto koreliacijos trūkumų. Paslaugos teikėjas ataskaitoje privalo pateikti kiekvienos matavimo įrangos ir matavimo metodikos aprašymą ir matavimo technologijos pasirinkimo pagrindimą.

    - Kontaktinių šaltinio lygmens ir objekto lygmens matavimo rezultatų palyginamosios ataskaitos parengimas ir pateikimas.

      - Paslaugos teikėjas privalo atlikti kontaktinių šaltinio lygmens matavimų palyginimą su objekto lygmens matavimų duomenimis. Pateikti palyginimo ataskaitą, kuri turi atitikti Reglamento reikalavimus ir OGMP 2.0 rekomendacijas. Ataskaita turi būti pateikta ne vėliau kaip per 20 (dvidešimt) kalendorinių  dienų po kontaktinių šaltinio lygmens ir objekto lygmens matavimų įvykdymo.

      - Atliekant kontaktinių šaltinio lygmens matavimų ir nepilno sudeginimo emisijų šaltinių matavimų palyginimą su objekto lygmens matavimų duomenimis, Paslaugos teikėjas turi įvertinti ir aprašyti aplinkos sąlygas, esamą technologinį procesą, sulyginti matavimų rezultatus, apskaičiuoti neatitiktis, paklaidas ir neapibrėžtumus, pateikti objekto palyginimo ataskaitą su išvadomis ir rekomendacijomis siekiant duomenų suderinamumo. Taip pat pateikti kiekvieno nepilno sudeginimo specifinius emisijos faktorius (kg/kWh) pagal matavimų duomenis (kg/h) ir momentinį sudegintą dujų srautą (kWh). Ataskaitoje pateikti matavimams naudotos įrangos aprašymą, naudotus matavimo metodus bei atliktus skaičiavimus.

      - Paslaugos teikėjas analizės metu turi identifikuoti į objektą patenkančio metano kiekį, nepriklausantį objektui ir jo netraukti į bendrą objekto metano emisijų skaičiavimą.

  - Bendri reikalavimai Paslaugų vykdymui:

    - Paslaugos teikėjas vykdydamas matavimus Pirkėjo fiziniuose objektuose turi laikytis Pirkėjo saugos ir sveikatos reikalavimų, atitinkamai pagal teikiamų Paslaugų pobūdį.

    - Pirkėjas neįsipareigoja Paslaugos teikėjui suteikti asmeninių apsaugos priemonių, matavimo prietaisų ar kitų Paslaugoms atlikti reikalingų įrengimų (stelažų ir pan.). Paslaugos teikėjo naudojama įranga (matavimo prietaisai ir įrenginiai, telefonas nuotraukoms atlikti) būtina numatytoms paslaugoms įvykdyti, turi būti tinkama naudoti sprogiose zonose ir turėti ATEX sertifikatą arba lygiavertį.

    - Paslaugos teikėjas į metano nuotėkių matavimų paslaugų kainas įtraukia visus kaštus būtinus tinkamam Paslaugų suteikimui (matavimo ar kitos būtinos įrangos nuoma, specialisto darbo laikas, duomenų apdorojimas, komandiruotės kaštai, transportas, skrydžių bilietai ar kt.).

    - Paslaugų teikėjas viso Sutarties vykdymo laikotarpiu privalo turėti ir taikyti apsaugos vadybos sistemos standarto EN ISO 14001 ar jam lygiaverčio standarto reikalavimus, kurios taikymo sritis apimtų metano emisijų matavimo ir (ar) dokumentavimo ir (ar) ataskaitų teikimo paslaugas.

    - Kadangi Teikėjui bus suteikiama informacija apie nacionaliniam saugumui užtikrinti svarbius įrenginius ir turtą, kurių atskleidimas gali kelti riziką ir grėsmę  Lietuvos Respublikos nacionaliniam saugumui, Paslaugų teikėjas, jo subtiekėjai, ūkio subjektai, kurių pajėgumais yra remiamasi, gamintojai, techninės ar programinės įrangos priežiūrą ir palaikymą atliekantys asmenys ar juos kontroliuojantys asmenys privalo  atitikti Lietuvos Respublikos nacionalinio saugumo reikalavimus numatytus 2002 m. spalio 10 d. Nr. IX-1132 įstatyme  „Lietuvos Respublikos nacionaliniam saugumui užtikrinti svarbių objektų apsaugos įstatymas“  (aktualia redakcija su vėlesniais pakeitimais) (nuoroda čia: Įstatymas )„bei 1996 m. rugpjūčio 13 d. Nr. I-1491 „Lietuvos Respublikos Viešųjų pirkimų įstatymas“   92 str. 14-15 dalimis.  (aktualia redakcija su vėlesniais pakeitimais) (nuoroda čia: VPĮ įstatymas) .

    - Pirkėjas suteiks prieigą Paslaugos tiekėjui prie Pirkėjo bendrosios duomenų aplinkos - Dalux, pagal Paslaugos tiekėjo pateiktą atsakingų darbuotojų sąrašą ne vėliau kaip per 14 (keturiolika) kalendorinių dienų. Bendroji duomenų aplinka (CDE – angl. Common Data Environment) bus naudojama kaip centrinė informacijos saugykla (suformuota debesijos principu), kurioje laikoma informacija reikalinga Paslaugų atlikimui – matavimo objektų sąrašas, matavimo taškų schemos, matavimų ataskaitos, nuotraukos, matavimo įrangos dokumentacija, darbų grafikai ir apimtys.

    - Visi Paslaugų vykdymo metu surinkti duomenys apie Pirkėjo objektą turi būti apdorojami tik Europos Sąjungoje. Visi surinkti duomenys turi išlikti konfidencialūs visą Sutarties galiojimo laikotarpį. Duomenys turi būti apsaugoti nuo neteisėto perėmimo ar panaudojimo, laikantis ES kibernetinio saugumo taisyklių (nuoroda – https://eur-lex.europa.eu/eli/dir/2022/2555/oj).

    - Paslaugos teikėjas įsipareigoja neatskleisti administruojamų duomenų, neperleisti tretiesiems asmenims ir užtikrinti kokybišką jų apsaugą visą Sutarties galiojimo laikotarpį.

    - Paslaugos teikėjas įsipareigoja, jog visa archyvinė informacija, Sutarties galiojimo laikotarpiu bus apsaugota nuo trečiųjų šalių ir pasibaigus Sutarties galiojimo terminui nemokamai ir saugiai perduota Pirkėjui  su Pirkėju suderintu formatu.

    - Pirkėjas yra visų surinktų duomenų savininkas. Paslaugos teikėjas įsipareigoja Pirkėjui pareikalavus ne vėliau kaip per 14 (keturiolika) kalendorinių dienų nuo Pirkėjo pareikalavimo momento, eksportuoti ir perduoti visus per visą Paslaugų vykdymo laikotarpį Paslaugų teikimo metu sukauptus duomenis (matavimų duomenys, inventoriaus hierarchijos duomenys, remonto užsakymai, stebėjimo ir remonto grafikai, ataskaitos ir kt.) su Pirkėju suderintu formatu (.xls, .csv ar kt.).

    - Paslaugos teikėjas įsipareigoja ne vėliau kaip per 21 (dvidešimt vieną) kalendorinę dieną negrįžtamai sunaikinti visus Pirkėjo pateiktus duomenis, Paslaugos teikėjo resursais surinktus duomenis apie Pirkėjo eksploatuojamus objektus, darbuotojų bei įrangos duomenis, matavimų duomenis, ataskaitas,  Pirkėjui pateikus rašytinį prašymą. Paslaugos teikėjas po duomenų sunaikinimo turi pateikti duomenų perdavimą ir sunaikinimą patvirtinantį pasirašytą oficialų raštą Pirkėjo atstovui el. paštu.

    - Pasibaigus Sutarties galiojimo terminui tarp Paslaugos teikėjo ir Pirkėjo, Paslaugos teikėjas privalo iš savo sistemos pašalinti visus sukauptus archyvinius duomenis, jų visas galimas kopijas ir neperduoti jų tretiesiems asmenims. Paslaugos teikėjas po duomenų sunaikinimo turi pateikti duomenų perdavimą ir sunaikinimą patvirtinantį pasirašytą oficialų raštą Pirkėjo atstovui el. paštu.

    - Apie bet kokius Paslaugos teikėjo infrastruktūroje galimus duomenų pasisavinimo, nutekėjimo ir (ar) kibernetinio saugumo incidentų  atvejus, Paslaugos teikėjas nedelsdamas, tačiau ne vėliau kaip per 2 (val.)  privalo informuoti Pirkėją el. paštu ir (arba) telefonu ir imtis visų įmanomų priemonių, situacijai suvaldyti.

- SUTARTINIŲ ĮSIPAREIGOJIMŲ VYKDYMO TVARKA IR TERMINAI:

  - Pirkėjas įsipareigoja ne vėliau kaip per 14 (keturiolika) kalendorinių  dienų nuo  Sutarties pasirašymo momento,  pateikti Paslaugos teikėjui šios techninės specifikacijos 6 skyriuje nurodytus dokumentus, kad būtų tinkamai atlikti dujų nuotėkių matavimo darbai.

  - Paslaugos teikėjas  ne vėliau kaip per 14 (keturiolika) kalendorinių  dienų, nuo šios techninės specifikacijos 6 skyriuje nurodytų dokumentų gavimo dienos, privalo pateikti ir su Pirkėju suderinti Paslaugų vykdymo grafiką. Grafikas turi būti pateikiamas dienų ir (ar) savaitės tikslumu, grafike numatyti veiksmai bei jų įgyvendinimo terminai gali būti koreguojami Paslaugos teikėjui pakeitimus iš anksto raštu suderinus su Pirkėju, tačiau galutinis Paslaugų įvykdymo terminas negali būti vėlesnis negu numatyta šios techninės specifikacijos 5.4.1 ir 5.4.2 punktuose. Grafikas turi būti parengtas skaitmeniniu .pdf, .xls, .docx arba lygiaverčiu formatu.

  - Pirkėjas planuoja užsakyti periodinius kontaktinius šaltinio lygmens matavimus, kaip numatyta šios techninės specifikacijos 4.2 skyriuje, DSS; DAS; DASRS; DSRM; DKS objektuose kas 4 (keturi)  mėn. (kas sudaro apie 75 objektus, preliminarus matavimo taškų kiekis  –77 000 vieno periodinio matavimo metu) bei ČA objektuose – kas 9 mėn. (kas sudaro apie 318 objektų, preliminarus matavimo taškų kiekis – 64 000 vieno periodinio matavimo metu). Preliminarus planuojamų užsakyti periodinių kontaktinių šaltinio lygmens matavimų grafikas pateiktas šios techninės specifikacijos 2 Priede. Preliminarus planuojamų matavimų grafikas gali būti koreguojamas, atnaujintą grafiką Paslaugos teikėjas ir Pirkėjas raštu  suderina po Sutarties pasirašymo, kaip numatoma šios techninės specifikacijos  5.2 punkte.

  - Paslaugos teikėjas įsipareigoja:

    - iki 2026 m. spalio 1 d. atlikti objekto lygmens matavimus kartu su kontaktiniais šaltinio lygmens matavimais, kaip numatyta šios techninės specifikacijos 4.2 ir 4.3 skyriuose (visuose DSS; DAS; DASRS; DSRM; DKS objektuose bei uždarymo įtaisų aikštelėse (apie 15-20 uždarymo įtaisų aikštelių)), pagal el. paštu suderintą su Pirkėju grafiką;

    - iki 2026 m. lapkričio 30 d. pateikti objekto lygmens ir kontaktinio šaltinio lygmens matavimų lyginamąsias ataskaitas kaip numatyta šios techninės specifikacijos 4.4.2 skyriuje.

  - Paslaugos teikėjui įvykdžius šios techninės specifikacijos 5.4.1. punkte numatytus matavimus, sekantys objekto lygmens matavimus kartu su kontaktiniais šaltinio lygmens matavimais preliminariai numatomi vykdyti 2027 ir 2028 metais. Tikslios 2027-2028 metais matuojamų objektų apimtys ir grafikas turi būti raštu suderintos ne vėliau kaip iki einamųjų metų kuriais atliekami matavimai vasario 28 d.

  - Pirkėjas neįsipareigoja užsakyti visų Paslaugos teikėjo Paslaugų visuose eksploatuojamuose objektuose, Paslaugos bus įsigyjamos pagal poreikį visą Sutarties galiojimo laikotarpį.

- SUTARTIES VYKDYMO METU PATEIKIAMA DOKUMENTACIJA:

  - AB „Amber Grid“ objektų sąrašas;

  - AB „Amber Grid“ objektų technologinės schemos;

  - AB „Amber Grid“ turto hierarchijos duomenys.

- PASLAUGŲ TRŪKUMŲ ŠALINIMO TVARKA IR TERMINAI:

  - Paslaugos tiekėjo pateiktų matavimo duomenų, ataskaitų ar fizinių matavimų trūkumai turi būti pašalinti per 7 (septynias) kalendorines dienas, nuo Pirkėjo pranešimo el. paštu išsiuntimo dienos.

- PRIEDAI:

Priedas Nr. 1 Fizinių objektų charakteristikos ir pageidautina matavimo įranga.

Priedas Nr. 2 Preliminarūs matavimų grafikai ir apimtys.

Priedas Nr. 3  Paslaugų preliminarūs kiekiai ir apimtys 36 mėn. laikotarpiui.

1 Priedas. Fizinių objektų charakteristikos ir pageidautina matavimo įranga.

| Eil. Nr. | Objektų grupė / objekto pavadinimas | Preliminarus objektų kiekis | Preliminarus matavimo taškų skaičius viename objekte | Metano nuotėkio matavimo taškų maksimalus aukštis, m* | Pageidautina objekto lygmens matavimo įranga | Pageidautina kontaktinio šaltinio lygmens matavimo įranga |
| --- | --- | --- | --- | --- | --- | --- |
| 1. | Jauniūnų dujų kompresorių stotis (JDKS) | 1 | 10 000 | Iki 20 m | Dronas su matavimo įranga arba lygiavertė technologija | Pasiekiamuose taškuose: nešiojamas nuotėkio koncentracijos detektorius FID arba PID arba TDLAS arba lygiavertė technologija (angl. sniffing device). Nepasiekiamuose taškuose: OGI arba lygiavertė technologija. |
| 2. | Panevėžio dujų kompresorių stotis (PDKS) kartu su Piniavos DSS | 1 | 3 500 | Iki 15 m | Dronas su matavimo įranga arba lygiavertė technologija |  |
| 3. | Dujų apskaitos ir slėgio reguliavimo stotis (DASRS) (Santaka) | 1 | 2 200 | Iki 4 m | Įvertina Paslaugos teikėjas |  |
| 4. | Dujų apskaitos stotis (DAS) (Šakiai) | 1 | 3 100 | Iki 7 m | Įvertina Paslaugos teikėjas |  |
| 5. | Dujų apskaitos stotis (DAS) (Kiemėnai) | 1 | 1 700 | Iki 4 m | Įvertina Paslaugos teikėjas, pageidautina matavimo įranga be drono arba lygiavertė technologija |  |
| 6. | Dujų apskaitos stotis (DAS) (Mažeikiai) | 1 | 550 | Iki 4 m | Įvertina Paslaugos teikėjas, pageidautina matavimo įranga be drono arba lygiavertė technologija |  |
| 7. | Dujų slėgio ribojimo mazgai (DSRM) – (Dauparai, Lapkasiai, Marijampolė) | 3 | Nuo 280 iki 400 viename objekte | Iki 4 m | Įvertina Paslaugos teikėjas, pageidautina matavimo įranga be drono arba lygiavertė technologija |  |
| 8. | Dujų skirstymo stotys (DSS) | 20 | Nuo 500 iki 1300 viename objekte | Iki 4 m | Įvertina Paslaugos teikėjas, pageidautina matavimo įranga be drono arba lygiavertė technologija |  |
| 9. | Dujų skirstymo stotys (DSS) | 25 | Nuo 500 iki 1300 viename objekte | Iki 5 m | Įvertina Paslaugos teikėjas |  |
| 10. | Dujų skirstymo stotys (DSS) | 18 | Nuo 500 iki 1300 viename objekte | Iki 15 m | Dronas su matavimo įranga arba lygiavertė technologija |  |
| 11. | Dujų skirstymo stotis (Vilniaus DSS kartu su Vilniaus DSRM) | 1 | 1 600 | Iki 10 m | Dronas su matavimo įranga arba lygiavertė technologija |  |
| 12. | Uždarymo įtaisų aikštelės (ČA) | 318 | Nuo 20 iki 800 viename objekte | Iki 4 m | Įvertina Paslaugos teikėjas, pageidautina matavimo įranga be drono arba lygiavertė technologija |  |

* - Pateikti preliminarūs maksimalaus matavimo taškų aukščio duomenys.

2 Priedas. Preliminarūs matavimų grafikai ir apimtys.

- Kontaktiniai šaltinio lygmens matavimai

  - DSS; DAS; DASRS; DSRM; DKS objektuose (apie 75 objektus).

PRELIMINARUS MATAVIMŲ PLANAS KAS 4 MĖNESIUS

2026 m. vasaris – kovas, jeigu yra pasirašyta Sutartis ir Paslaugos Teikėjas turi technines galimybes suplanuoti, pasiruošti ir atlikti matavimus (preliminarus matavimo taškų kiekis 77 000);

2026 m. birželis – liepa (preliminarus matavimo taškų kiekis 77 000);

2026 m. spalis – lapkritis (preliminarus matavimo taškų kiekis 77 000);

2027 m. vasaris – kovas (preliminarus matavimo taškų kiekis 77 000);

2027 m. birželis – liepa (preliminarus matavimo taškų kiekis 77 000);

2027 m. spalis – lapkritis (preliminarus matavimo taškų kiekis 77 000);

2028 m. vasaris – kovas (preliminarus matavimo taškų kiekis 77 000);

2028 m. birželis – liepa, jeigu yra galiojanti Sutartis (preliminarus matavimo taškų kiekis 77 000);

2028 m. spalis – lapkritis, jeigu yra galiojanti Sutartis (preliminarus matavimo taškų kiekis 77 000).

  - ČA objektuose (apie 318 objektų).

PRELIMINARUS MATAVIMŲ PLANAS KAS 9 MĖNESIUS

2026 m. vasaris – kovas – balandis, jeigu yra pasirašyta Sutartis ir Paslaugos Teikėjas turi technines galimybes suplanuoti, pasiruošti ir atlikti matavimus (preliminarus matavimo taškų kiekis 64 000);

2026 m. lapkritis – gruodis – 2027 m. sausis (preliminarus matavimo taškų kiekis 64 000);

2027 m. rugpjūtis – rugsėjis – spalis (preliminarus matavimo taškų kiekis 64 000);

2028 m. gegužė – birželis – liepa, jeigu yra galiojanti Sutartis (preliminarus matavimo taškų kiekis 64 000).

- Objekto lygmens matavimai kartu su kontaktiniais šaltinio lygmens matavimais.

PRELIMINARUS MATAVIMŲ PLANAS KASMET

2026 METAI.

Iki 2026 m. spalio 1 d. atlikti matavimus visuose DSS; DAS; DASRS; DSRM; DKS objektuose (detalesni duomenys apie matuojamus objektus pateikti 1 Priede) bei su Pirkėju suderintose uždarymo įtaisų aikštelėse (apie 15-20 objektų);

2027 ir 2028 METAI.

Tikslios 2027-2028 metais matuojamų objektų apimtys ir matavimo grafikas bus raštu suderintas tarp Paslaugos teikėjo ir Pirkėjo ne vėliau kaip iki einamųjų metų kuriais atliekami matavimai vasario 28 d.

Pastaba: pateiktas grafikas ir apimtys yra preliminarūs, Pirkėjas neįsipareigoja užsakyti visų nurodytų matavimų.

3 priedas. Paslaugų preliminarūs kiekiai  ir apimtys 36 mėn. laikotarpiui:

| Eil. Nr. | Pirkimo objektas | Matavimo vienetai | Preliminarus kiekis 36 mėn.*** |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 2026 m. | 2027 m. | 2028 m. | VISO |
| 1 | Kontaktiniai periodiniai šaltinio lygmens metano nuotėkių matavimai (kaip numatyta techninės specifikacijos 4.2 skyriuje ir 2 Priedo 1 punkte) | Matavimo taškas | 218 000 | 295 000 | 295 000 | 731 000 |
| 2 | Neeilinis iškvietimas (kaip numatyta techninės specifikacijos 4.2.12 punkte) | 1 darbuotojo iškvietimas | 1 | 1 | 1 | 3 |
| 3 | Kontaktinių šaltinio lygmens metano nuotėkių matavimų ataskaita (kaip numatyta techninės specifikacijos 4.4.1 skyriuje) | Ataskaita | 1 | 1 | 1 | 3 |
| 4 | Objekto lygmens metano nuotėkių matavimai su dronais ar lygiaverte technologija (kaip numatyta techninės specifikacijos 4.3 skyriuje ir 2 Priedo 2 punkte) | Objektai | 25 | 25 | 25 | 75 |
| 5 | Objekto lygmens metano nuotėkių matavimai kitomis priemonėmis (kaip numatyta techninės specifikacijos 4.3 skyriuje ir 2 Priedo 2 punkte) | Objektai | 50 | 50 | 50 | 150 |
| 6 | Objekto lygmens ir kontaktinių šaltinio lygmens matavimo rezultatų palyginamoji ataskaita (kaip numatyta techninės specifikacijos 4.4.2 skyriuje) | Ataskaita | 4 | 4 | 4 | 12 |

*** Nurodytas kiekis yra preliminarus visam Sutarties galiojimo laikotarpiui. Pirkėjas Paslaugas įsigis pagal poreikį, neįsipareigojant išpirkti viso nurodyto preliminaraus kiekio per visą sutarties galiojimo laikotarpį, tad preliminarus kiekis gali didėti arba mažėti, priklausomai nuo Pirkėjo poreikio.

TECHNICAL SPECIFICATION

PROCUREMENT OF SERVICES FOR THE MEASUREMENT OF NATURAL GAS (METHANE) LEAKS, DATA ANALYSIS, AND REPORT PREPARATION

- DEFINITIONS AND ABBREVIATIONS

Buyer - AB “Amber Grid”. More information about the Buyer and its activities can be found at www.ambergrid.lt

Supplier - an economic entity - natural person, private legal person, public legal person, other organisations and their subdivisions or a group of such persons, with which the Buyer enters into an Agreement.

Services – natural gas (methane) leak detection, data analysis, and report preparation services.

Agreement – an agreement entered into between the Service Provider and the Buyer for the provision of services related to the measurement of natural gas (methane) leaks, data analysis, and the preparation of reports;

Regulation – Regulation (EU) 2024/1787 of the European Parliament and of the Council of 13 June 2024 on the reduction of methane emissions in the energy sector, amending Regulation (EU) 2019/942 (reference – Regulation - EU - 2024/1787 - EN - EUR-Lex);

An extraordinary call-out - an urgent, extraordinary call-out to conduct methane leak measurements.

Abbreviations:

EPA 21 – A testing method approved by the United States Environmental Protection Agency EPA Method 21;

LST EN 15446:2008 – a Lithuanian standard corresponding to the European standard EN 15446:2008;

ES - European Union

OGMP 2.0 – The Oil & Gas Methane Partnership 2.0 (reference – Resources | The Oil & Gas Methane Partnership 2.0);

JGCS– Jauniūnai Gas Compressor Station

PGCS– Panevėžys Gas Compressor Station

GDS – Gas Distribution Station;

GMS – Gas metering station;

GMPRS – Gas metering and pressure regulation station;

GPRU – Gas pressure regulating units;

SEP – Shut-off equipment platform;

ppm – A unit of concentration (parts per million).

- PROCUREMENT OBJECT

  - Procurement object – services for measuring natural gas (methane) leaks, data analysis, and report preparation (hereinafter - the Services).

  - The Procurement object cannot be divided into parts. The Service provider must offer the entire quantity/scope of the Procurement object.

  - The Procurement object includes the following services:

    - services for measuring methane leaks at the source and object levels at the Buyer’s physical objects;

    - services for the analysis of measurement data and the preparation of reports.

  - The Buyer seeks to purchase Services whose technical requirements are described in this Technical specification, in the Agreement to be concluded, and in accordance with the parameters and conditions set forth in the procurement documents.

- SCOPE AND CHARACTERISTICS OF THE PROCUREMENT

  - Preliminary dimensions of the objects to be measured:

    - Jauniūnai Gas Compressor Station*;

    - Panevėžys Gas Compressor Station*;

    - Gas distribution stations*;

    - Gas metering stations*;

    - Gas metering and pressure regulation station*;

    - Gas pressure relief valves*;

    - Shut-off equipment platform*.

The estimated volumes of measurement points (potential sources of natural gas (methane) leaks) at the sites are listed in Table 1.

Table 1. Preliminary number of measurement points in physical objects.

| No. | Object* | Estimated number of measurement points** | Notes |
| --- | --- | --- | --- |
| 1. | Jauniūnai Gas Compressor Station (JGCS) | 10,000 | The measurements must be taken in relation to the operating mode of the compressors. |
| 2. | Panevėžys Gas Compressor Station (PGCS) | 3,500 | The measurements must be taken in relation to the operating mode of the compressors. |
| 3. | Gas distribution stations (GDS) – 64 Gas metering stations (GMS) – 3 (Kiemėnai, Šakiai, Mažeikiai) Gas metering and pressure regulation station (GMPRS) (Santaka) Gas pressure regulating units (GPRU) – 4 (Dauparai, Lapkasiai, Vilnius, Marijampolė) | 63,500 | - |
| 4. | Shut-off equipment platform (SEP) - 318 | 64,000 | - |
| In total: |  | 141,000 |  |

Notes:

*A detailed list of locations will be provided to the Service provider during the term of the Agreement, following the signing of the Agreement.

**Table 1 provides preliminary figures for the number of measurement points at the sites.

- REQUIREMENTS FOR THE PROCUREMENT OBJECT

  - Measurements of natural gas (methane) leaks at the source level and site level must be carried out in accordance with the requirements of standard EN 15446 (or an equivalent standard) and in accordance with Regulation (EU) 2024/1787 of the European Parliament and of the Council of 13 June 2024 Regulation (EU) 2024/1787 of the European Parliament and of the Council on the reduction of methane emissions in the energy sector, amending Regulation (EU) 2019/942 (hereinafter - the Regulation) and taking into account the guidelines The Oil & Gas Methane Partnership 2.0 (hereinafter – OGMP 2.0).

  - On-site measurements of source-level methane leaks at the Buyer’s physical objects.

    - The Service provider, using the best available methodology for contact measurements (Type 2) (using EPA21 or LST EN 15446:2008 or equivalent) and the best measurement tools available on the market, must identify potential methane leakage points, taking into account the recommendations set forth in the OGMP 2.0 guidelines and the requirements established in the Regulation.

    - The measuring instruments used for measurements must comply with the requirements of the Regulation (current version, as amended).

    - Measurements must be performed using the direct (contact) method (Type 2), using calibrated equipment with a minimum detection limit of no more than 1 ppm (e.g., FID, PID, TDLAS, or equivalent technology) that directly measures methane concentration in parts per million (ppm).

    - If a measurement point cannot be checked directly because it is difficult to access and this poses a risk to employee safety, the Service provider must select measurement methods as provided for in the Regulation (current version with subsequent amendments) and perform the measurements using other methods (e.g., OGI or equivalent technologies).

    - The Service provider, using its own equipment and resources and in accordance with the agreed work schedule, must inspect the potential methane leak points specified in detail in Table 1 of these Technical specifications. Assign the measurement results to the corresponding objects in the inventory hierarchy.

    - During the measurement, the Service provider must physically mark the components of the equipment where methane leaks are detected with a purple label, regardless of the size of the leaks.

    - The Service provider must photograph the identified and marked locations where methane leaks have been detected. The photograph must clearly indicate the location of the leak.

    - If the Service provider identifies any discrepancies between the physical methane leak measurement points and the technical diagram, it shall notify the Buyer within 5 (five) calendar days and send the diagram with the discrepancies marked to the Buyer via email.

    - During the physical measurements, the Service provider must provide the Buyer with weekly reports on detected gas leaks and the status of the measurements. The Service provider must specify the measured leak rate in ppm when providing information, for all detected gas leaks, regardless of their size, the object identification code and the measurement point identification code based on asset hierarchy data, a photograph of the leak location, the date and time of the measurement, the measuring device, and information about the operator who performed the measurements. The data template for the information provided is set out in Table 2 of these Technical specifications.

    - The Service provider must identify which detected leaks are related to process venting (VENT) and which are caused by component leaks or malfunction (LEAK).

    - The Service provider’s employees will be accompanied to the Buyer’s premises to perform measurements after coordinating with the Buyer’s designated representatives no later than 14 (fourteen) calendar days in advance. During the measurements, the Buyer’s designated representatives may carry out repairs on any gas leaks that are detected. In such a case, the Service provider must perform a repeat measurement on the same or the next working day following the repair. The Service provider must record the data from the initial measurement, the repair, and the repeat measurement in detail in the reports. The Service provider must follow the procedure for granting permission to work established by the Buyer, which can be found here: Procedure for Granting Permission to Work.

    - The Buyer may order the Service provider’s measurement services for an extraordinary, urgent methane leak detection (hereinafter - an Extraordinary Call-out). If there is a need to carry out an Extraordinary call-out for methane leak detection, the Buyer shall submit a request via email to the Service provider, specifying the scope of the measurement requirements. The Service provider’s employee must arrive to perform the measurements no later than 14 calendar days from the date the request for an Extraordinary call-out was submitted. The Service provider includes all relevant expenses (travel expenses, transportation, flight tickets, etc.) in the standard rate for an Extraordinary Call-out. In the case of an Extraordinary Call-out, payment to the Service provider for the methane leak measurement work performed shall be made in accordance with the standard rates provided (as specified in points 1, 4, or 5 of Annex 3), plus the standard rate for an Extraordinary Call-out (as specified in point 2 of Annex 3).

    - The template table for presenting measurement data, provided in Table 2 of these Technical specifications, may be adapted and modified; fields may be added or revised, provided that the Service provider coordinates such revisions and changes with the Buyer.

Table 2. Template for the data submission form.

| Object ID | Filled in for all measurement points |
| --- | --- |
| Measurement point ID | Filled in for all measurement points |
| Measurement result | Filled in for all measurement points |
| Unit of measure for the measurement result | Filled in for all measurement points |
| Measurement date | Filled in for all measurement points |
| Measurement time | Filled in for all measurement points |
| Measurement performed by | Filled in for all measurement points |
| Measuring device | Filled in for all measurement points |
| Significance of the leak | Filled in only after a gas leak has been detected (under repair or being monitored) |
| Leak type | Filled in only after a gas leak has been detected (venting or leak) |
| Detailed description of the leak location | Filled in only after recording a gas leak, if applicable |
| Repairs were carried out immediately | Filled in for all measurement points |
| Measurement result after repair | Filled in only for repaired points |
| Unit of measurement for the measurement result after repair | Filled in only for repaired points |
| Measurement date | Filled in only for repaired points |
| Measurement time | Filled in only for repaired points |
| Measurement performed by | Filled in only for repaired points |
| Measuring device | Filled in only for repaired points |

  - On-site methane leak measurements at the Buyer’s physical objects.

    - The Service provider must measure the Buyer’s sites using the best available site-level measurement methodology, employing its own and/or leased equipment, in accordance with the recommendations set forth in the OGMP 2.0 guidelines and the requirements established in the Regulation.

    - The measuring instruments used for measurements must comply with the requirements of the Regulation (current version, as amended).

    - Site-level methane leakage measurements must be conducted at the same time as point-source methane leakage measurements to ensure the most accurate comparison of data.

    - The Service provider must take weather conditions into account to ensure that measurements are taken only under safe and optimal conditions and in accordance with the manufacturers’ instructions for the measuring instruments.

    - The Service provider must assess the situation and select the most appropriate measuring equipment, taking into account the characteristics of the Buyer’s various sites.

    - Shut-off equipment platforms are installed in open outdoor areas, while GCS, GDS, GMS, GMPRS, and GPRU objects are located indoors; however, they also include outdoor equipment that may serve as potential sources of methane leaks. Of the 65 gas distribution stations, 35 are housed in containers, while the rest are housed in larger containers or buildings. More detailed information on methane leakage measurement points at physical sites is provided in Annex 1 of this Technical specification.

    - The Service provider must ensure that, when conducting object-level measurements at physical objects, all potential sources of methane leakage and sources of incomplete combustion emissions—namely, emissions from gas-fired boilers—are measured.

  - Preparation and submission of reports on completed measurements.

    - Preparation and submission of reports on source-level measurements.

      - The Service provider must analyze the measurements and prepare a template for the measurement report. The report must include the quantitative leakage values per unit of time (g/h) and concentration measurement values (ppm) for the measured locations (points), the object identification code and the measurement point identification code based on asset hierarchy data, the measurement date and time, the measuring instrument, information about the operator who performed the measurements, location information, the technical number of the pipeline or other facility, diameter, medium, and point location, with a reference to the technical diagrams linked to the hierarchy. The report template must be agreed upon in writing with the Buyer before physical measurements are taken at the sites. The report must be submitted no later than 20 (twenty) calendar days after the contact source level measurements have been completed.

      - If the Service provider has converted units of measurement when preparing the report, it must provide the conversion methodology, which must comply with applicable international standards, along with a detailed explanation, uncertainties, coefficients (if used in the conversion), and calculation errors to avoid flow correlation errors. The Service provider must include in the report a description of each piece of measuring equipment and measurement methodology, as well as a justification for the choice of measurement technology.

    - Preparation and submission of a comparative report on the results of source-level and site-level measurements.

      - The Service provider must compare the source-level measurements with the object-level measurement data. Submit a comparison report that complies with the requirements of the Regulation and the OGMP 2.0 recommendations. The report must be submitted no later than 20 (twenty) calendar days after the completion of measurements at the source level and the object level.

      - When comparing contact-level source measurements and measurements of incomplete combustion emission sources with object-level measurement data, the service provider must assess and describe the environmental conditions and the existing technological process, reconcile the measurement results, calculate discrepancies, errors, and uncertainties, and submit a site comparison report with conclusions and recommendations to ensure data consistency. Also provide the specific emission factors for each incomplete combustion (kg/kWh) based on the measurement data (kg/h) and the instantaneous gas flow rate (kWh). The report should include a description of the equipment used for the measurements, the measurement methods employed, and the calculations performed.

      - During the analysis, the Service provider must identify the amount of methane entering the object that is not attributable to the object and exclude it from the overall calculation of the object’s methane emissions.

  - General Requirements for the Provision of Services:

    - The Service provider, when performing measurements at the Buyer's physical premises, must comply with the Buyer's health and safety requirements, as appropriate to the nature of the Services provided.

    - The Buyer is not obligated to provide the Service provider with personal protective equipment, measuring instruments, or other equipment necessary for the performance of the Services (such as scaffolding, etc.). The equipment used by the Service provider (measuring instruments and devices, a camera for taking photographs) is necessary for the performance of the agreed services, must be suitable for use in explosive atmospheres, and must have ATEX certification or an equivalent.

    - The Service provider includes all costs necessary for the proper provision of methane leak measurement services in its pricing (rental of measurement or other necessary equipment, specialist labor, data processing, travel expenses, transportation, airfare, etc.).

    - Throughout the entire term of the Agreement, the Service provider must maintain and apply the requirements of the EN ISO 14001 environmental management system standard or an equivalent standard, the scope of which covers services related to the measurement and/or documentation and/or reporting of methane emissions.

    - Since the Service provider will be provided with information regarding equipment and assets that are important for ensuring national security, the disclosure of which may pose a risk or threat to the national security of the Republic of Lithuania, the Service provider, its sub-suppliers, economic operators whose capabilities are relied upon, manufacturers, persons performing hardware or software maintenance and support, or persons controlling them must  comply with the national security requirements of the Republic of Lithuania set forth in Law No. IX-1132 of 10 October 2002, the “Law on the Protection of Objects of Importance to Ensuring National Security of the Republic of Lithuania” (current version with subsequent amendments) (link here:  Law and Article 92 ( 14–15) of Law No. I-1491 of 13 August 1996, “Law on Public Procurement of the Republic of Lithuania”      (current version with subsequent amendments) (link here:  Law on PP) .

    - The Buyer shall grant the Service provider access to the Buyer’s general data environment—Dalux—in accordance with the list of authorized employees provided by the Service provider, no later than within 14 (fourteen) calendar days.  The Common Data Environment (CDE) will serve as a central information repository (based on cloud computing principles) containing the information necessary for the provision of services—a list of measurement objects, measurement point diagrams, measurement reports, photographs, measurement equipment documentation, work schedules, and scopes of work.

    - All data regarding the Buyer’s object collected during the provision of the Services must be processed exclusively within the European Union. All collected data must remain confidential for the entire duration of the Agreement. Data must be protected against unauthorized access or use in accordance with EU cybersecurity regulations (link – https://eur-lex.europa.eu/eli/dir/2022/2555/oj).

    - The Service provider undertakes not to disclose the data it manages, not to transfer it to third parties, and to ensure its effective protection throughout the term of the Agreement.

    - The Service provider undertakes to ensure that all archived information is protected from third parties during the term of the Agreement and, upon expiration of the Agreement, is transferred to the Buyer free of charge and securely in a format agreed upon with the Buyer.

    - The Buyer is the owner of all collected data. The Service provider undertakes, at the Buyer’s request, to export and transfer all data accumulated during the provision of the Services throughout the entire Service provision period (measurement data, inventory hierarchy data, repair orders, monitoring and repair schedules, reports, etc.) in a format agreed upon with the Buyer (.xls, .csv, etc.).

    - The Service provider undertakes to irrevocably destroy all data provided by the Buyer no later than within 21 (twenty-one) calendar days, data collected using the Service provider’s resources regarding the Buyer’s objects, employee and equipment data, measurement data, and reports,  upon the Buyer’s written request. After destroying the data, the Service provider must send a signed official letter confirming the transfer and destruction of the data to the Buyer’s representative via email.

    - Upon expiration of the Agreement between the Service provider and the Buyer, the Service provider must delete all stored archived data and any copies thereof from its system and must not disclose such data to third parties. After destroying the data, the Service provider must send a signed official letter confirming the transfer and destruction of the data to the Buyer’s representative via email.

    - In the event of any data theft, leakage, and/or cybersecurity incidents within the Service provider’s infrastructure, the Service provider must immediately, but no later than within 2 (hours), notify the Buyer by e-mail and/or telephone and take all possible measures to manage the situation.

- PROCEDURES AND DEADLINES FOR THE FULFILLMENT OF CONTRACTUAL OBLIGATIONS:

  - The Buyer agrees to submit to the Service provider, no later than 14 (fourteen) calendar days from the date of signing the Agreement, the documents specified in Section 6 of these technical specifications, so that the gas leak measurement work can be properly performed.

  - The Service provider must submit a schedule for the performance of the Services and agree upon it with the Buyer no later than within 14 (fourteen) calendar days from the date of receipt of the documents specified in Section 6 of these Technical specifications. The schedule must be provided with daily and/or weekly precision; the actions specified in the schedule and their deadlines may be adjusted provided that the Service provider coordinates any changes with the Buyer in advance in writing, however, the final deadline for the performance of the Services may not be later than that specified in Sections 5.4.1 and 5.4.2 of these Technical specifications. The schedule must be provided in digital .pdf, .xls, .docx or equivalent format.

  - The Buyer plans to order periodic on-site source-level measurements, as specified in Section 4.2 of these Technical specifications, at GDS, GMS, GMPRS, GPRU, and GCS objects every 4 (four) months (which amounts to approximately 75 objects, with a preliminary number of measurement points of 77,000 per periodic measurement) and at SEP objects —every 9 months (which amounts to approximately 318 objects, with a preliminary number of measurement points of 64,000 per periodic measurement). A preliminary schedule for the planned periodic source-level measurements is provided in Annex 2 of this Technical specification. The preliminary schedule of planned measurements may be adjusted; the Service provider and the Buyer shall agree on the updated schedule in writing after the signing of the Agreement, as provided for in Section 5.2 of theseTechnical specifications.

  - The Service provider undertakes to:

    - By 1 October 2026, perform object-level measurements together with contact source-level measurements, as specified in Sections 4.2 and 4.3 of these technical specifications (at all GDS, GMS, GMPRS, GPRU, GCS objects and at switching yards (approximately 15–20 switching yards)), in accordance with the schedule agreed upon with the Buyer by e-mail;

    - Submit comparative reports on object-level and contact source-level measurements by 30 November 2026, as specified in Section 4.4.2 of these Technical specifications.

  - Once the Service provider has completed the measurements specified in Section 5.4.1 of these Technical specifications, the subsequent object-level measurements, together with the contact source-level measurements, are tentatively scheduled to be carried out in 2027 and 2028. The exact scope and schedule of the properties to be surveyed in 2027–2028 must be agreed upon in writing no later than 28 February of the current year in which the surveys are to be conducted.

  - The Buyer is not obligated to order all of the Service provider’s Services at all of its operating objects. The Services will be purchased as needed throughout the term of the Agreement.

- DOCUMENTATION PROVIDED DURING THE PERFORMANCE OF THE AGREEMENT:

  - List of objects of AB “Amber Grid”;

  - Technological diagrams of AB "Amber Grid" objects;

  - AB “Amber Grid” asset hierarchy data.

- PROCEDURE AND TIMELINES FOR RESOLVING SERVICE DEFICIENCIES:

  - Any deficiencies in the measurement data, reports, or physical measurements provided by the Service provider must be rectified within 7 (seven) calendar days from the date the Buyer sends the notification by email.

- ANNEXES:

Annex No. 1 Characteristics of physical objects and recommended measurement equipment.

Annex No. 2 Preliminary measurement schedules and scopes.

Annex No. 3 Preliminary quantities and scopes of services for a 36-month period.

Annex 1. Characteristics of physical objects and recommended measurement equipment.

| No. | Group of objects / object name | Estimated number of objects | Estimated number of measurement points per object | Maximum height of methane leak measurement points, m* | Preferred object-level measurement equipment | Preferred contact source-level measurement equipment |
| --- | --- | --- | --- | --- | --- | --- |
| 1. | Jauniūnai Gas Compressor Station (JGCS) | 1 | 10,000 | Up to 20 m | A drone equipped with measurement equipment or equivalent technology | At accessible points: a portable FID, PID, or TDLAS leak concentration detector, or equivalent technology (sniffing device). In hard-to-reach areas: OGI or equivalent technology. |
| 2. | Panevėžys Gas Compressor Station (PGCS) together with the Piniava Gas Distribution System | 1 | 3,500 | Up to 15 m | A drone equipped with measurement equipment or equivalent technology |  |
| 3. | Gas metering and pressure regulation station (GMPRS) (Santaka) | 1 | 2,200 | Up to 4 m | Rated by the Service Provider |  |
| 4. | Gas metering station (GMS) (Šakiai) | 1 | 3,100 | Up to 7 m | Evaluated by the Service Provider |  |
| 5. | Gas metering station (GMS) (Kiemėnai) | 1 | 1,700 | Up to 4 m | Evaluated by the Service provider; preferably using measurement equipment without a drone or equivalent technology |  |
| 6. | Gas metering station (GMS) (Mažeikiai) | 1 | 550 | Up to 4 m | Evaluated by the Service provider; preferably using measurement equipment without a drone or equivalent technology |  |
| 7. | Gas pressure regulating units (GPRU) – (Dauparai, Lapkasiai, Marijampolė) | 3 | From 280 to 400 per site | Up to 4 m | Evaluated by the Service provider; preferably using measurement equipment without a drone or equivalent technology |  |
| 8. | Gas distribution stations (GDS) | 20 | From 500 to 1,300 per site | Up to 4 m | Evaluated by the Service provider; preferably using measurement equipment without a drone or equivalent technology |  |
| 9. | Gas distribution stations (GDS) | 25 | From 500 to 1,300 per site | Up to 5 m | Evaluated by the Service Provider |  |
| 10. | Gas distribution stations (GDS) | 18 | From 500 to 1,300 per site | Up to 15 m | A drone equipped with measurement equipment or equivalent technology |  |
| 11. | Gas distribution station (Vilnius GDS together with Vilnius GPRU) | 1 | 1,600 | Up to 10 m | A drone equipped with measurement equipment or equivalent technology |  |
| 12. | Shut-off equipment platforms (SEP) | 318 | From 20 to 800 per site | Up to 4 m | Evaluated by the Service provider; preferably using measurement equipment without a drone or equivalent technology |  |

* - Preliminary data on the maximum height of measurement points is provided.

Annex 2. Preliminary measurement schedules and scopes.

- Contact measurements at the source level

  - GDS; GMS; GMPRS; GPRU; GCS objects (approximately 75 objects).

PRELIMINARY MEASUREMENT PLAN EVERY 4 MONTHS

February–March 2026, provided that the Agreement has been signed and the Service provider has the technical capacity to plan, prepare, and carry out the measurements (estimated number of measurement points: 77,000);

June–July 2026 (estimated number of measurement points: 77,000);

October– November 2026 (estimated number of measurement points: 77,000);

February– March 2027 (estimated number of measurement points: 77,000);

June–July 2027 (estimated number of measurement points: 77,000);

October– November 2028 (estimated number of measurement points: 77,000);

February– March 2028 (estimated number of measurement points: 77,000);

June–July 2028, provided that a valid Agreement is in place (estimated number of measurement points: 77,000);

October–November 2028, provided that a valid Agreement is in place (estimated number of measurement points: 77,000).

  - At SEP objects (approximately 318 objects).

PRELIMINARY MEASUREMENT PLAN EVERY 9 MONTHS

February–March–April 2026, provided that the Agreement has been signed and the Service provider has the technical capacity to plan, prepare, and carry out the measurements (estimated number of measurement points: 64,000);

November–December 2026 – January 2027 (estimated number of measurement points: 64,000);

August–September–October 2027 (estimated number of measurement points: 64,000);

May–June–July 2028, provided that a valid Agreement is in place (estimated number of measurement points: 64,000).

- Object-level measurements in conjunction with contact source-level measurements.

PRELIMINARY MEASUREMENT PLAN FOR EACH YEAR

YEAR 2026

By 1 October 2026, perform measurements at all GDS, GMS, GMPRS, GPRU, and GCS objects (detailed information on the objects to be measured is provided in Annex 1) and at the switching station sites agreed upon with the Buyer (approximately 15–20 objects);

THE YEARS 2027 AND 2028.

The exact scope of the objects to be measured in 2027–2028 and the measurement schedule shall be agreed upon in writing between the Service provider and the Buyer no later than by 28 February of the current year in which the measurements are to be performed.

Note: The schedule and quantities provided are preliminary; the Buyer is not obligated to order all of the specified measurements.

Annex  3. Estimated quantities and volumes of services for a 36-month period:

| No. | Procurement object | Measurement units | Estimated quantity for 36-months***: |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 2026 | 2027 | 2028 | IN TOTAL |
| 1 | Periodic contact measurements of source-level methane emissions (as specified in Section 4.2 of the Technical specifications and Clause 1 of Annex 2) | Measurement point | 218,000 | 295,000 | 295,000 | 731,000 |
| 2 | Extraordinary call-out (as provided for in Section 4.2.12 of the Technical specifications) | Call-out for 1 employee | 1 | 1 | 1 | 3 |
| 3 | Report on measurements of methane leaks at the source level (as specified in Section 4.4.1 of the Technical specifications) | Report | 1 | 1 | 1 | 3 |
| 4 | Site-level methane leakage measurements using drones or equivalent technology (as specified in Section 4.3 of the Technical specifications and Clause 2 of Annex 2) | Objects | 25 | 25 | 25 | 75 |
| 5 | Measurements of methane emissions at the object level using other methods (as specified in Section 4.3 of the Technical specifications and Clause 2 of Annex 2) | Objects | 50 | 50 | 50 | 150 |
| 6 | Comparative report on measurement results at the object level and at the contact source level (as specified in Section 4.4.2 of the Technical specifications) | Report | 4 | 4 | 4 | 12 |

*** The quantity specified is preliminary for the entire term of the Agreement. The Buyer will purchase the Services as needed, without committing to purchase the entire specified preliminary quantity over the entire term of the Agreement; therefore, the preliminary quantity may increase or decrease depending on the Buyer’s needs.