PERKANČIOSIOS ORGANIZACIJOS ATSAKYMAS Į TIEKĖJO PAKLAUSIMĄ

Gynybos resursų agentūra prie Krašto apsaugos ministerijos (toliau – perkančioji organizacija) 2025 m. gegužės 7 d. Centrinėje viešųjų pirkimų informacinėje sistemoje (toliau – CVP IS) (pirkimo Nr. 7719239) paskelbė Elektros generatorių pirkimo atvirą konkursą (toliau – pirkimas), kuris vykdomas CVP IS priemonėmis, pasiekiamomis adresu https://viesiejipirkimai.lt/.

Pirkimas skaidomas į 6 (šešias) pirkimo dalis:

1 pirkimo dalis – nešiojamas 6 kW elektros generatorius;

2 pirkimo dalis – nešiojamas 10 kW elektros generatorius;

3 pirkimo dalis – mobilus 20 kW elektros generatorius su priekaba;

4 pirkimo dalis – mobilus 50 kW elektros generatorius su priekaba;

5 pirkimo dalis – mobilus 100 kW elektros generatorius su priekaba;

6 pirkimo dalis – mobilus 200 kW elektros generatorius su priekaba.

Perkančioji organizacija CVP IS priemonėmis gavo tiekėjo paklausimą (tekstas neredaguotas):

„We kindly ask you to clarify the point 3.15.10. below for the engine coolant pre-heater.

The question applies only to the gensets of 20, 50 and 100 kW:

Given that low-power diesel generators typically have a 12 V DC electrical system (battery, starter motor and charging generator), it would be technically correct/appropriate to amend the requirements of the second part of clause 3.15.10. as follows:

“3.15.10. Pre-heating of engine coolant prior to start-up with a built-in 230 V AC electric heater and 12 V or 24 V DC diesel heater “.

At the same time, compliance with the requirements of clauses 3.20 and 3.21 remain in force, and diesel generators will be equipped with the required accessories to enable the units to be started from an external 24 V DC source (for this purpose, a suitable 24/12 V DC converter will be installed on the gensets). Nothing will change functionally for the end user.

We ask for acceptance to use 12 V DC diesel heaters, provided that the requirements of clauses 3.20 and 3.21 are met.

This does not affect the 200 kW units, as units of such power and higher are with 24V electrical system, due to their large capacity.

Thank you in advance for feedback..“

Perkančiosios organizacijos atsakymas į paklausimą:

Public procurement legislation allows for the establishment of specific technical specification requirements where such requirements are necessary for the contracting authority to procure what it needs. It should be noted that the requirements set out in sub-clause 3.15.10 of Annex 1 “Technical Specification” to the procurement documents (applicable to Lots 3–5) reflect the needs of the end user – the Lithuanian Armed Forces.

In view of the above, the contracting authority will not amend the requirements set out in sub-clause 3.15.10 of Annex 1 “Technical Specification” to the procurement documents (applicable to Lots 3–5). It should be noted that the mobile 20 kW, 50 kW, and 100 kW power generators offered by tenderers must comply with the requirements established in the technical specification.

Viešuosius pirkimus reglamentuojantys teisės aktai leidžia nustatyti specifinius techninės specifikacijos reikalavimus, jei tai yra būtina norint perkančiajai organizacijai įsigyti tai, ko jai reikia. Pažymėtina, kad reikalavimai nustatyti pirkimo sąlygų 1 priedo „Techninė specifikacija” 3.15.10 papunktyje (taikoma 3-5 pirkimo dalims) atliepia tiesioginio naudotojo - Lietuvos kariuomenės, poreikį.

Atsižvelgiant į aukščiau išdėstytą, perkančioji organizacija nekeis reikalavimų, nustatytų pirkimo sąlygų 1 priedo „Techninė specifikacija” 3.15.10 papunktyje (taikoma 3-5 pirkimo dalims). Pažymėtina, kad dalyvių siūlomi mobilūs 20 kW, 50 kW ir 100 kW elektros generatoriai turi atitikti techninėje specifikacijoje nustatytus reikalavimus.

Viešojo pirkimo komisija