PERKANČIOSIOS ORGANIZACIJOS ATSAKYMAI Į TIEKĖJO PAKLAUSIMĄ IR PIRKIMO PROCEDŪRŲ NUTRAUKIMAS 2 PIRKIMO DALYJE

Gynybos resursų agentūra prie Krašto apsaugos ministerijos (toliau – perkančioji organizacija) 2025 m. gegužės 7 d. Centrinėje viešųjų pirkimų informacinėje sistemoje (toliau – CVP IS) (pirkimo Nr. 7719239) paskelbė Elektros generatorių pirkimo atvirą konkursą (toliau – pirkimas), kuris vykdomas CVP IS priemonėmis, pasiekiamomis adresu https://viesiejipirkimai.lt/.

Pirkimas skaidomas į 6 (šešias) pirkimo dalis:

1 pirkimo dalis – nešiojamas 6 kW elektros generatorius;

2 pirkimo dalis – nešiojamas 10 kW elektros generatorius;

3 pirkimo dalis – mobilus 20 kW elektros generatorius su priekaba;

4 pirkimo dalis – mobilus 50 kW elektros generatorius su priekaba;

5 pirkimo dalis – mobilus 100 kW elektros generatorius su priekaba;

6 pirkimo dalis – mobilus 200 kW elektros generatorius su priekaba.

Perkančioji organizacija CVP IS priemonėmis gavo tiekėjo paklausimą (tekstas neredaguotas):

„We kindly ask you to specify a few aspects regarding requirements for the portable 10 kW generators (Lot 2):

Clause 1.1 states that the genset must be of an ‘open-type’ (i.e. not enclosed in a canopy), but clause 3.12 specifies a noise level of 75 dB(A) at a distance of 7 meters.

As a manufacturer of diesel generators, we carry out noise measurements during factory acceptance test (FAT) and we are aware of what noise level of an open portable generator is - generally for this power rating it is around 85-95 dB(A), in case of an open type solution.
To ensure the specified 75 dB(A), the unit must be housed in a canopy or shell (not an ‘open-type’ unit).

Thus, the above mentioned points clearly contradict one another. There are, of course, diesel engines designed specifically with noise reduction, but these essentially also have a soundproof casing and a unit based on them cannot be considered an ‘open-type’.
We kindly ask you to clarify what is exactly needed - we presume that the "open type" description is a mistake.“

Perkančiosios organizacijos atsakymas į paklausimą:

Informuojame, kad rengiant pirkimo sąlygų 1 priede pateiktą nešiojamojo 10 kW elektros generatoriaus techninę specifikaciją (2 pirkimo dalis) buvo padaryta esminė klaida 3.12 punkte nustatant reikalavimą dėl generatoriaus skleidžiamo triukšmo lygio ir, vadovaujantis Lietuvos Respublikos viešųjų pirkimų įstatymo (toliau – VPĮ) 36 straipsnio 6 dalies nuostatomis, atitinkamos padėties negalima ištaisyti.

Vadovaujantis VPĮ 29 straipsnio 4 dalimi, pirkimo procedūros 2 pirkimo dalyje nutraukiamos, nes pirkimo dokumentuose padaryta esminių klaidų, dėl kurių nebūtų įmanoma įvertinti gautų pasiūlymų nepažeidžiant principų, nurodytų VPĮ 17 straipsnio 1 dalyje, o pirkimą įvykdžius būtų įsigytas perkančiosios organizacijos poreikių neatitinkantis pirkimo objektas.

Vadovaujantis VPĮ 29 straipsnio 2 dalies 3 punktu, pirkimo procedūros 2 pirkimo dalyje laikomos pasibaigusiomis.

Prašytume neteikti pasiūlymo 2 pirkimo daliai, o jei pasiūlymas šiai daliai jau pateiktas, tiekėjas jį turi atsiimti, pakoreguoti pasiūlymą dėl nutrauktos 2 pirkimo dalies ir pateikti iš naujo. Kitu atveju pasiūlymai nutrauktoje 2 pirkimo dalyje nebus vertinami ir bus automatiškai atmesti.

We hereby inform you that, during the preparation of the technical specification for the portable 10 kW power generator set out in Annex 1 to the procurement documents (Lot 2), a material error was made in Clause 3.12 regarding the requirement for the generator’s noise emission level. In accordance with Article 36(6) of the Law on Public Procurement of the Republic of Lithuania (hereinafter – the PPL), the situation cannot be remedied.
Pursuant to Article 29(4) of the PPL, the procurement procedures for Lot 2 are hereby terminated, as the procurement documents contain material errors which would make it impossible to evaluate the submitted tenders without violating the principles set out in Article 17(1) of the PPL, and completion of the procurement would result in the acquisition of a procurement object that does not meet the contracting authority’s needs.
In accordance with Article 29(2)(3) of the PPL, the procurement procedures for Lot 2 shall be deemed concluded.
We kindly request that no tender be submitted for Lot 2. If a tender for this lot has already been submitted, the supplier must withdraw it, revise the proposal relating to the terminated Lot 2, and resubmit them. Otherwise, tenders submitted for the terminated Lot 2 will not be evaluated and will be automatically rejected.

Viešojo pirkimo komisija