# TECHNICAL SPECIFICATION

# FOR THE SUPPLY AND INSTALLATION

# OF A SOLAR POWER PLANT WITH ENERGY STORAGE SYSTEM

The Central Project Management Agency is carrying out a public procurement procedure for the supply and installation of a solar photovoltaic power plant with battery energy storage. The works, goods and services offered by the suppliers must comply with the requirements set out in this Technical Specification.

| Nr. | Features | Technical specification requirements | Documents proving compliance with the requirement | Exact parameters of the proposed object (if applicable, tick the relevant boxes and/or provide the requested information) |
| --- | --- | --- | --- | --- |
|  | General requirements for the subject of the contract |  |  |  |
| 1.1. | Subject of purchase | Supply and installation of a solar photovoltaic power plant 30 kW with battery energy storage system 40 kWh to ensure a constant supply of electricity to the building (hereafter referred to as the solar power plant/solar power system) | The supplier declares compliance with this requirement in the next column of the table | ☐ We confirm that we understand the purpose of the item to be procured and that we offer the following works, goods and services in accordance with the requirements set out below. |
| 1.2. | Final Beneficiary | Zhytomyr Rehabilitation Center | The supplier declares compliance with this requirement in the next column of the table | ☐ We confirm that we understand that the work and services to be procured are for the final beneficiary of the Facility referred to in this point. |
| 1.3. | Delivery and installation location/address | Delivery and installation of the solar power system at the site at: 22 Feshchenko-Chopivskoho St., Zhytomyr, Ukraine. | The supplier declares compliance with this requirement in the next column of the table | ☐ We confirm that we will deliver, install and provide other related services necessary for the purchase of the solar power system proposed by us for the specified property at the specified address. |
| 1.4. | Time limit | The whole of the work to be procured under this procurement must be completed within a maximum of 5 months from the start date of the works. Work may begin no earlier than 1 October 2026. | The supplier declares compliance with this requirement in the next column of the table. | ☐ We confirm that the whole of the work to be procured under this procurement will be completed within a maximum of ____ months from the start date of the works. The works may commence no earlier than 15 August 2026. |
| 1.5. | Equipment | The proposed equipment must be new and unused. Used or used and refurbished equipment cannot be offered. 1. The equipment must have been manufactured no earlier than 24 months before the date of actual delivery of the equipment to the installation site. 2. The Supplier delivering the goods will be required to provide documentation confirming the date of manufacture of the goods. | The supplier declares compliance with this requirement in the next column of the table. | ☐ 1. We confirm that all equipment offered will be delivered and installed new, unused and unrefurbished. The equipment will be manufactured no earlier than 24 months prior to the date of actual delivery of the equipment to the installation site. ☐ 2. We confirm that we will provide, at the time of delivery of the goods, documentation confirming the date of manufacture of the goods. |
| 1.6. | Warranty | - Photovoltaic modules must be guaranteed for at least 20 years. - The photovoltaic module mounting structures must be guaranteed for at least 10 years. - The manufacturer's guarantee of the efficiency of the photovoltaic modules after 25 years of operation shall not be less than 80,0 %. - Inverters (voltage converters) must be guaranteed for at least 5 years. - The battery system must be guaranteed for at least 10 years or for at least 6 000 charge/discharge cycles with a residual capacity of at least 60% of the nominal capacity after the guarantee period. (The warranty must cover manufacturing defects, degradation above the specified level and malfunctioning due to the manufacturer.) - The monitoring system and its software must operate smoothly for at least 10 years. The warranty must cover all functional components, including the LTE/5G (or equivalent) module, the data storage and the main functions of the system. - At least 5-year warranty for the work carried out and 10-year warranty for hidden elements (structures, engineering systems, etc.). - Other equipment and materials - at least 2 years warranty | The supplier declares compliance with this requirement in the next column of the table. | We offer the following warranty conditions for the solar power system: - The photovoltaic modules are guaranteed for ___ years. - The photovoltaic module mounting structures shall be guaranteed for ___ years. - The manufacturer's guarantee of the efficiency of the PV modules after 25 years of operation shall be ___ %. - Inverters (voltage converters) shall be guaranteed for ___ years. - The battery system shall be warranted for ___ years or a minimum of ______ charge/discharge cycles with a residual capacity of at least ___ % of the nominal capacity after the warranty period (Warranty covers factory defects, degradation above the specified level, and malfunctioning due to the manufacturer.) - The monitoring system and its software will operate smoothly for at least ___ years. The warranty covers all functional components including LTE/5G (or equivalent) module, data storage and the main functions of the system. - The work performed shall be covered by a ___ year warranty and a ___ year warranty for hidden elements (structures, engineering systems, etc.). - Other equipment and materials - ___ year warranty. |
| 1.7. | Cybersecurity requirements | 1. The entire proposed solar power system, including inverters, battery management system, monitoring equipment and control modules (the "System"), must ensure secure data transmission and secure remote access. 2. The system must be isolated from public networks or connected through secure network firewalls to reduce the risk of cyber-attacks. 3. Authentication and access control: the system must ensure that access is only possible through secure authentication procedures (e.g. using unique user identifiers and strong passwords). Measures must be in place to restrict unauthorized access to equipment and the network. 4. Data security: all data communication between System components (e.g. inverter, batteries, monitoring equipment) and external networks shall be encrypted using secure protocols (e.g. TLS, HTTPS). 5. Software updates and vulnerability management: the Supplier shall ensure that regular software updates, including security patches, are applied to the entire System. The Supplier shall ensure that the system is kept operational and up-to-date free of charge for at least 10 years from the date of installation. 6. Incident monitoring and management: the system must be configured to detect and monitor unusual activity, such as unauthorized connections or equipment malfunctions. | The supplier declares compliance with this requirement in the next column of the table. | ☐ We confirm that we have read, fully understood and incorporated into our offer the technical requirements and conditions provided. The proposed equipment and solutions comply with the specified requirements. |
| 1.8. | Description of the current situation | The works must be carried out in accordance with the submitted project, which specifies specific quantities, functionalities and requirements, the participant must evaluate all the necessary works, materials and necessary functionalities when preparing the proposal and submit a commercial offer for equivalent or not worse equipment specified in the prepared project. Also: - The solar photovoltaic modules and other equipment shall be installed on the roof of a building in accordance with the attached project. - The solar power system with batteries installed by the supplier must be seamlessly connected (integrated) into the existing infrastructure of the building in accordance with the project, and must ensure uninterrupted power supply both in the event of normal operation and in the event of a power outage, in autonomous mode (using the energy generated by the solar power plant or the energy stored in the batteries) - For information and for the proper preparation of the offer, the available building information shall be given to the Supplier for an accurate assessment of the locations for the connection of the solar power plant as specified in the Technical Specification, as well as for the placement and connection of the equipment and batteries: ANNEXES: Attached files in an archived electronic file: “Annex technical documentation.zip” | The supplier declares compliance with this requirement in the next column of the table. | ☐ We confirm that we have familiarized ourselves with the current situation of the building and that we have made a proper assessment of all the circumstances necessary for the delivery and installation of the solar power system. |
| 1.9. | Scope of Work | - The Supplier must provide all materials, equipment and installation works and services necessary for the complete, operational installation of the system in accordance with the Technical Specification. This includes additional components or actions that may not be explicitly identified but are necessary for the functioning of the system. All works shall be carried out in a logical sequence and the components of the system shall be coordinated with each other. - The Supplier must draw up the work plan and coordinate its execution (if required by the beneficiary's law). Ensure that the works are carried out in accordance with the design, the technological plan and the manufacturers' instructions. Protect works in progress and completed works from damage, moisture, temperature, freezing, etc. Must protect surrounding buildings from damage, dust and dirt. Properly sorts and disposes of construction waste. Ensures the health and safety of workers. Coordinate the project with the beneficiary before the start of work. The products must be stored under the conditions specified by the manufacturer and on site in suitable, dry, ventilated, heated (if necessary) premises. Damaged or improperly stored goods must be replaced at the Supplier's expense. - Installation and supplementary design works (if required): The solar photovoltaic power plant and the battery energy storage system shall be installed in accordance with the attached technical project documentation, applicable Ukrainian legislation and technical requirements. The Supplier shall assess and include in the tender all minor supplementary, adaptation, detailing or installation design works that may be necessary for the proper, complete and operational implementation of the project documentation and integration of the system into the existing infrastructure. All supplementary design solutions, if required, shall be coordinated with the Beneficiary and other competent authorities where required under applicable legislation. The works shall include all activities specified in the technical specification and all other works necessary for complete installation, integration, testing, commissioning, configuration and proper operation of the facility, even if certain minor components or works are not explicitly indicated in the project documentation. If applicable under Ukrainian legislation, the Supplier shall also be responsible for arranging and obtaining any required permits, approvals, expertise, or other mandatory authorizations related to the implementation works. | The supplier declares compliance with this requirement in the next column of the table. | ☐ We confirm that we have read, fully understood and included in our proposal the technical requirements and conditions provided. The proposed equipment, works, services, design and solutions are in conformity with the specified requirements. |
| 1.10. | Compliance with Legal Requirements | The supplier must comply with all applicable regulatory requirements at all stages of work (design, equipment delivery, execution of works). All materials must meet the standards applicable to their type and be certified in at least one EU or EEA country or have an equivalent document. Certificates must be provided to the Buyer upon request. | The supplier declares compliance with this requirement in the next column of the table. | ☐ We confirm that we have reviewed the provided technical requirements and conditions, fully understood them, and have incorporated them into our proposal. The proposed equipment, works, and solutions meet the specified requirements. |
| 1.11. | Training | After completing all the work, the supplier must train at least one representative of the beneficiary on how to use and operate the system, and provide access credentials to the system. | The supplier declares compliance with this requirement in the next column of the table. | ☐ We confirm that after completing all the work, we will train at least one representative of the beneficiary on how to use and operate the system, and will provide the necessary access credentials to the system. |
| 2. | Technical Requirements for the Procurement Object – Solar Photovoltaic Power Plant |  |  |  |
| 2.1. | Solar photovoltaic power plant output: | No less than 30 kW | The supplier declares compliance with this requirement in the next column of the table. The supplier must also provide the manufacturer's technical documentation in Lithuanian or English (catalogs, brochures) and/or the manufacturer's declarations of conformity (if the manufacturer's technical documentation does not fully reflect the compliance of the proposed product with the technical specification requirements) or other equivalent documents proving the compliance of the proposed product with the technical requirements. In these documents, the supplier must graphically highlight (i.e., visibly mark – using color, arrows, and/or underlining) specific sections of the submitted documents where the required technical characteristics are described and indicate which technical requirement point they comply with. The Contracting authority has the right to request the originals of the catalogs and technical descriptions. | The proposed Solar photovoltaic Power plant output is ____ kW. Please specify which document is provided and the specific location within it where the compliance with the requirement is confirmed: ______________________________________. |
| 2.2. | Photovoltaic Module Manufacturer and Photovoltaic Modules | The photovoltaic modules must have properties that are at least as good as monocrystalline modules or equivalent. All photovoltaic modules must be of the same type, of the same power, and from the same manufacturer. | The same requirements as in point 2.1. | Type, name, manufacturer of the photovoltaic modules: ___________________________, Power of one photovoltaic module ____ kW. Document and specific location confirming compliance with the requirement: ______________________________________. |
| 2.3. | Efficiency of Photovoltaic Modules according to STC (Standard Test Conditions), %: | At least 20% | The same requirements as in point 2.1. | Efficiency of Photovoltaic Modules according to STC (Standard Test Conditions) ___ % Document and specific location confirming compliance with the requirement: ______________________________________. |
| 2.4. | Photovoltaic module layout, mounting location, mounting method and design | - When submitting a tender, supplier must: - The layout, orientation and mounting locations of photovoltaic modules are defined in the attached project documentation. - The Supplier shall review the proposed technical solutions and verify their compatibility with the actual site conditions before installation works. - The mounting structures used shall be made of robust, durable materials resistant to corrosion, environmental impact and aging throughout the entire service life. - If minor adjustments to the mounting or layout solutions become necessary during implementation due to actual site conditions, such adjustments shall be coordinated with the Beneficiary. | The same requirements as in point 2.1. | ☐ We confirm that we have reviewed the provided technical requirements and conditions, fully understood them, and incorporated them into our proposal. The proposed equipment and solutions meet the specified requirements. |
| 2.5. | Inverters (voltage converters) | The proposed inverters (voltage converters) shall comply with the requirements of these standards: • EN 50549-1:2019, or equivalent. • IEC 62109-1:2010 and IEC 62109-2:2011, or equivalent standards. • IEC 62116:2014 or equivalent. Inverters (voltage converters): - must be compatible with the installed solar power system and its total capacity. - must be compatible with the installed energy storage (battery) system. - The system with the inverter(s) must have the capability to deliver surplus electricity to the public power grid, if such a need or opportunity arises. If this is not possible now or in the future, the system must operate autonomously in a closed-loop mode, appropriately regulating electricity flows — i.e., delivering the generated electricity to the building and/or storage system, and in case of a shortage, drawing the required electricity from the public grid or storage system, based on real-time needs and with operating priorities agreed upon with the beneficiary. - The system must have the capability to connect to an external generator. | The same requirements as in point 2.1. | Inverters name, manufacturer, model: ___________________________ Inverters comply with the following standards: ______________________________________ ☐ 1. We confirm that the proposed inverters (voltage converters) are suitable and will be matched with the installed solar power system and its total capacity. ☐ 2. We confirm that the proposed inverters (voltage converters) are suitable and will be matched with the proposed and installed energy storage (battery) system. ☐ 3. We confirm that the system with the inverter(s) will have the capability to deliver surplus electricity to the public power grid, if such a need or opportunity arises. If this is not possible now or in the future, the system will operate autonomously in a closed-loop mode, regulating electricity flows accordingly — i.e., supplying the generated electricity to the building and/or storage system, and in the event of a shortage, drawing the required electricity from the public grid or storage system, based on the current needs and with operating priorities agreed upon with the beneficiary. ☐ 4. We confirm that the system will have the capability to connect to an external generator. Documents and specific references confirming compliance with the requirements: _______________________________________. |
| 2.6. | Lightning protection | If it is not possible to maintain a safe distance between the solar modules and the lightning rods and lightning protection elements, the supplier will be obliged to make corrections to the lightning protection system at its own cost and to ensure adequate lightning protection (if such a system is installed in the building). | The supplier declares compliance with this requirement in the next column of the table. | ☐ We confirm that we have assessed the need for lightning protection adjustments, should such a need arise during installation. |
| 2.7. | Surge protection, earthing | Surge protectors must be provided on the 0,4kV AC side and the DC side. Surge protection and earthing systems must comply with IEC 62305 or equivalent. The equipment and structures of the solar power plant must be properly earthed. | The supplier declares compliance with this requirement in the next column of the table. | ☐ We confirm that we have reviewed the provided technical requirements and conditions, fully understood them, and incorporated them into our proposal. The proposed equipment and solutions meet the specified requirements. |
| 2.8. | IP protection class | Photovoltaic modules: Junction boxes: ≥ IP65 protection class (or equivalent). Cable connections: ≥ IP65 protection class (or equivalent). Inverters (voltage converters):≥ IP65 protection class (or equivalent). | The same requirements as in point 2.1. | Photovoltaic modules: Junction boxes: IP__ protection class. Cable connections: IP__ protection class. Inverters (voltage converters): IP__ protection class. Documents and specific references confirming compliance with the requirements: _______________________________________. |
| 2.9. | CE compliance | Equipment must comply with CE requirements. The supplier shall provide a CE declaration of conformity. | The same requirements as in point 2.1. | ☐ We confirm that the equipment complies with CE requirements. Documents and specific references confirming compliance with the requirements: _______________________________________. |
| 3. | Technical Requirements for the Procurement Object – Battery energy storage system (batteries) |  |  |  |
| 3.1. | Battery Energy Storage System (batteries) capacity: | Total capacity of no less than 40 kWh. | The supplier declares compliance with this requirement in the next column of the table. The supplier must also provide the manufacturer's technical documentation in Lithuanian or English (catalogs, brochures) and/or the manufacturer's declarations (if the technical documentation does not fully reflect compliance of the proposed product with the technical specification requirements), or other equivalent documents proving the proposed product's compliance with the technical requirements. In these documents, the supplier must clearly mark (i.e., visibly highlight — using color, arrows, and/or underlining) the specific sections of the submitted documents that describe the required technical specifications, and indicate which point(s) of the technical requirements they correspond to. The contracting authority reserves the right to request the originals of catalogs and technical descriptions. | Proposed Battery Energy Storage System (batteries)name: ___________________, total capacity: ____ kWh. Please specify which submitted document and the exact location within it confirms compliance with the requirement: ____________________. |
| 3.2. | Chemical composition | The battery system must consist of lithium iron phosphate type batteries or a technology that: - meets at least the safety requirements of IEC 62619 (or an equivalent standard); - does not require periodic technical maintenance during operation (excluding software updates and automatic balancing function); - ensures a charge and discharge current rate of no less than 0.5C (if this complies with the system's operational requirements); - the battery system ensures at least 6,000 charge–discharge cycles, after which the remaining capacity is no less than 60% of the nominal capacity; - if the proposed battery system is not based on lithium iron phosphate (LiFePO₄, LFP) technology, documents confirming compliance with the IEC 62485-2 standard must be provided. | The same requirements as in point 3.1. | The battery system consists of ____________ type batteries or a technology that: 1. meets safety requirements in accordance with the ____________ standard; 2. ☒ does not require periodic technical maintenance during operation (excluding software updates and automatic balancing function); 3. ensures a charge and discharge current rate of ___; 4. the battery system ensures ______ charge–discharge cycles, after which the remaining capacity is ____ % of the nominal capacity; 5. if the proposed battery system is not based on lithium iron phosphate technology, documents confirming compliance with the IEC 62485-2 standard are provided. Documents and specific references confirming compliance with the requirements: _______________________________________. |
| 3.3. | Battery pack | Batteries must be modular, with the ability to change individual modules during servicing for ease of operation. The individual battery modules must be replaceable without the need for special equipment. If special equipment is required, it must be supplied with the equipment to be installed by the Supplier. | The supplier declares compliance with this requirement in the next column of the table. | ☐ We confirm that the batteries are modular, with the ability to change individual modules during servicing for ease of operation. The individual battery modules are replaceable without the need for special equipment. If special equipment is required, it will be supplied with the equipment to be installed by the Supplier. |
| 3.4. | Location of battery installation | The Supplier must select and evaluate the optimal location for the installation of the batteries, in agreement with the beneficiary, to ensure the efficient and smooth operation of the entire power plant system (unless otherwise specified in the project). | The supplier declares compliance with this requirement in the next column of the table. | ☐ We confirm that we will select and evaluate the optimal location for the installation of the batteries, in agreement with the beneficiary, to ensure the efficient and smooth operation of the entire power plant system. |
| 3.5. | Isolated operation | There must be a seamless automatic transition between operation when connected to the power system and autonomous operation (when disconnected from the power system). (The requirement to ensure a seamless automatic transition between connection to the energy system and autonomous operation (with a transition time of ≤100 ms) applies to the entire electricity generation and storage system as an integrated solution.) | The supplier declares compliance with this requirement in the next column of the table. | ☐ We confirm that the proposed system ensures a seamless automatic transition between operation when connected to the power system and autonomous operation (when disconnected from the power system). |
| 3.6. | Automatic synchronization | Automatic synchronization with the power grid must be ensured after the return to operation and connection to the power system. The synchronization time shall not exceed 10 seconds and the system shall ensure the stability of the grid frequency and voltage throughout the process. | The supplier declares compliance with this requirement in the next column of the table. | ☐ We confirm that automatic synchronisation with the power grid is ensured after the return to operation and connection to the power system. The synchronisation time is ___ seconds and the system ensures the stability of the grid frequency and voltage throughout the process. |
| 3.7. | DC circuit breakers | DC circuit breakers and protection against overload, short-circuit and overvoltage shall be provided. All DC protection devices shall be suitable for the actual system voltage, current and configuration of the installed solar photovoltaic and battery energy storage system. | The supplier declares compliance with this requirement in the next column of the table. | ☐ We confirm that DC circuit breakers and protection against overload, short-circuit and overvoltage shall be provided. All DC protection devices shall be suitable for the actual system voltage, current and configuration of the installed solar photovoltaic and battery energy storage system. |
| 3.8. | Managing priority users | The system must be configured to prioritize the critical systems of the building in autonomous operation mode (e.g. heating, lighting, IT systems, ventilation). | The supplier declares compliance with this requirement in the next column of the table. | ☐ We confirm that the system will be configured to prioritize the critical systems of the building in autonomous operation mode (e.g. heating, lighting, IT systems, ventilation). |
| 3.9. | Security | Not less than IP55 (or equivalent standard) for components installed outdoors or in areas exposed to dust and water. | The supplier declares compliance with this requirement in the next column of the table. | ☐ We confirm that not less than IP55 security will be ensured for components installed outdoors or in areas exposed to dust and water. |
| 3.10. | CE compliance | Equipment must comply with CE requirements. The supplier shall provide a CE declaration of conformity. | The same requirements as in point 3.1. | ☐ We confirm that equipment complies with CE requirements Documents and specific references confirming compliance with the requirements: _______________________________________. |
| 4. | Technical Requirements for the Procurement Object – Compatibility with Existing Building Infrastructure |  |  |  |
| 4.1. | Automatic transition: | The system must ensure smooth automatic transition between autonomous mode and normal electricity supply from the grid (and vice versa). If solar energy production or grid capacity is insufficient, energy stored in batteries must be used. | The supplier declares compliance with this requirement in the next column of the table. | ☐ We confirm that we have reviewed the provided technical requirements and conditions, fully understood them, and incorporated them into our proposal. The proposed equipment and solutions meet the specified requirements. |
| 4.2. | Synchronization: | Automatic synchronization with grid voltage, frequency, and power parameters must be ensured when switching between solar, battery, and grid power supply modes. | The supplier declares compliance with this requirement in the next column of the table. | ☐ We confirm that we have reviewed the provided technical requirements and conditions, fully understood them, and incorporated them into our proposal. The proposed equipment and solutions meet the specified requirements. |
| 4.3. | Priorities: | Preliminary energy supply priorities must be set as follows: a. Use of solar energy – solar-generated energy should be used first to meet user demand directly. b. Electricity from the grid – if solar generation is insufficient, the energy needs should be covered by the grid, provided it is available and reliable. c. Use of battery energy – to compensate for shortages when solar and grid energy are insufficient, unless otherwise agreed with the beneficiary during programming. | The supplier declares compliance with this requirement in the next column of the table. | ☐ We confirm that we have reviewed the provided technical requirements and conditions, fully understood them, and incorporated them into our proposal. The proposed equipment and solutions meet the specified requirements. |
| 4.4. | Stability and protection: | The system shall provide stable operation under variable loads, including protection against synchronisation errors, overloads and short circuits. | The supplier declares compliance with this requirement in the next column of the table. | ☐ We confirm that we have reviewed the provided technical requirements and conditions, fully understood them, and incorporated them into our proposal. The proposed equipment and solutions meet the specified requirements. |
| 4.5. | Control: | Energy flow management must be automated and optimized to ensure maximum use of solar energy and battery efficiency. | The supplier declares compliance with this requirement in the next column of the table. | ☐ We confirm that we have reviewed the provided technical requirements and conditions, fully understood them, and incorporated them into our proposal. The proposed equipment and solutions meet the specified requirements. |
| 5. | Technical Requirements for the Procurement Object – Requirements for the monitoring system |  |  |  |
| 5.1. | Mandatory monitoring system | The solar power system, including the inverters, the battery management system and all major components (the "System"), must be integrated with a monitoring system to ensure data collection, analysis and management of the System via both web and mobile application. | The supplier declares compliance with this requirement in the next column of the table. | ☐ We confirm that we have reviewed the provided technical requirements and conditions, fully understood them, and incorporated them into our proposal. The proposed equipment and solutions meet the specified requirements. |
| 5.2. | Monitoring indicators | The monitoring system must ensure that at least the following parameters can be monitored and displayed: 1. Total electricity generated. 2. Instantaneous power generation. 3. Voltage and current qualitative indicators (e.g. voltage level, harmonics, frequency). 4. The amount of electricity generated in the selected period. 5. Battery status, including charge/discharge level and remaining capacity. 6. Fault monitoring and diagnostics. 7. System efficiency indicators (e.g. kWh/kWp). | The supplier declares compliance with this requirement in the next column of the table. | ☐ We confirm that we have reviewed the provided technical requirements and conditions, fully understood them, and incorporated them into our proposal. The proposed equipment and solutions meet the specified requirements. |
| 5.3. | Data transmission and storage | The system must ensure that all data is transmitted using encrypted protocols (e.g. TLS, HTTPS). The monitoring system must have a local data repository to ensure data collection and storage for a period of at least 30 days, even in the event of a network connection failure. | The supplier declares compliance with this requirement in the next column of the table. | ☐ We confirm that we have reviewed the provided technical requirements and conditions, fully understood them, and incorporated them into our proposal. The proposed equipment and solutions meet the specified requirements. |
| 5.4. | Providing faults and warnings | The system must have real-time alerting of faults via email, SMS or mobile app. A history of failures shall be stored and available for analysis. | The supplier declares compliance with this requirement in the next column of the table. | ☐ We confirm that we have reviewed the provided technical requirements and conditions, fully understood them, and incorporated them into our proposal. The proposed equipment and solutions meet the specified requirements. |
| 5.5. | Communication technologies | The control unit of the solar power plant must be equipped with an LTE/5G module (or equivalent) to communicate with the monitoring system. In case of insufficient mobile connectivity, the system shall support an alternative connectivity solution, such as a local Wi-Fi network or wired connection. | The supplier declares compliance with this requirement in the next column of the table. | ☐ We confirm that we have reviewed the provided technical requirements and conditions, fully understood them, and incorporated them into our proposal. The proposed equipment and solutions meet the specified requirements. |
| 5.6. | Ease of use of the system | The monitoring system must have an intuitive and user-friendly interface, accessible via a computer or a mobile app. The supplier must configure user access. | The supplier declares compliance with this requirement in the next column of the table. | ☐ We confirm that we have reviewed the provided technical requirements and conditions, fully understood them, and incorporated them into our proposal. The proposed equipment and solutions meet the specified requirements. |
| 6. | Technical Requirements for the Procurement Object – Documentation (submitted together with the proposal or during contract execution) |  |  |  |
| 6.1. | Technical documentation: | - Documents prepared by the manufacturer of the goods (technical descriptions, certificates, passports, etc.). - System installation drawings and diagrams (originals and digital copies). - A list of the materials used, in digital format (indicating: name of the product/item, code, quantity, manufacturer, etc.) - All documents and formats to be submitted must be agreed in advance with the Buyer. | The supplier declares compliance with this requirement in the next column of the table. | ☐ We confirm that we have reviewed the provided technical requirements and conditions, fully understood them, and incorporated them into our proposal. The proposed equipment and solutions meet the specified requirements. |
| 6.2. | Software and login details: | - Original or copies of all software licenses (if applicable). - Monitoring system login details (usernames, passwords, configuration files). - Cables and interfaces required for connection (if the equipment has programmable components). | The supplier declares compliance with this requirement in the next column of the table. | ☐ We confirm that we have reviewed the provided technical requirements and conditions, fully understood them, and incorporated them into our proposal. The proposed equipment and solutions meet the specified requirements. |
| 6.3. | Operational documentation: | - System operation and maintenance manual in Ukrainian and English (1 hard copy and 1 electronic copy). - Warranty documents for all system components (e.g. modules, inverters, batteries, monitoring system). | The supplier declares compliance with this requirement in the next column of the table. | ☐ We confirm that we have reviewed the provided technical requirements and conditions, fully understood them, and incorporated them into our proposal. The proposed equipment and solutions meet the specified requirements. |
| 6.4. | Documentation of the work carried out: | - Completion certificates and their annexes (detailed list of works and installation). - All documents and formats to be submitted must be agreed in advance with the Buyer. | The supplier declares compliance with this requirement in the next column of the table. | ☐ We confirm that we have reviewed the provided technical requirements and conditions, fully understood them, and incorporated them into our proposal. The proposed equipment and solutions meet the specified requirements. |
| 6.5. | Certificates and test reports: | - A system commissioning certificate confirming proper operation. - Certificates of conformity of equipment to standards. - Electrical safety test reports (e.g. grounding, surge protection tests). | The supplier declares compliance with this requirement in the next column of the table. | ☐ We confirm that we have reviewed the provided technical requirements and conditions, fully understood them, and incorporated them into our proposal. The proposed equipment and solutions meet the specified requirements. |
| 6.6. | Work project | The solar photovoltaic power plant with a battery energy storage system shall be installed in accordance with the attached project documentation, applicable legal acts and technical requirements of Ukraine. The system must be properly connected and integrated into the existing building infrastructure and engineering systems, including but not limited to: - Preparation of all supplementary, adaptation, detailing, installation and as-built documentation necessary for the proper implementation, installation, commissioning and operation of the system; - Coordination of technical solutions with the Beneficiary and, where required under the applicable legislation of Ukraine, with all relevant authorities, institutions and organizations; - Execution of all works specified in the Technical Specification and attached project documentation, as well as all additional works, materials, components, configuration, testing, commissioning and adjustment works necessary to ensure complete, safe and uninterrupted operation of the facility and integration of all elements into one fully functioning system, even if certain minor works or components are not explicitly indicated in the Technical Specification or project documentation. All project documentation shall be handed over to the Beneficiary. | The supplier declares compliance with this requirement in the next column of the table. | ☐ We confirm that we have reviewed the provided technical requirements and conditions, fully understood them, and incorporated them into our proposal. The proposed equipment and solutions meet the specified requirements. |
| 6.7. | Proposal documentation | Together with the proposal (and other documentation specified in the technical specification), the supplier must submit a detailed cost estimate for the proposed works and services, clearly indicating at least the models and quantities of the proposed equipment. | The supplier declares compliance with this requirement in the next column of the table. Detailed cost estimate of the proposal. | ☐ 1. Together with the proposal, we provide a detailed cost estimate for the proposed works and services: ________________. |

NOTES:

If the technical specification or attached project documentation indicates a specific model or source of supply, a particular process characteristic of goods or services provided by a specific supplier, or a trademark, standard, patent, type, specific origin, or manufacturer, suppliers may propose an equivalent alternative. The supplier must demonstrate the equivalence as specified in this section.

If specific technical characteristic values (parameters) are indicated in the technical specification, suppliers may offer goods whose values (parameters) are not inferior to those specified (i.e., goods with characteristics that are not worse may be offered).

In case of discrepancies between the Technical Specification and the attached project documentation, the attached project documentation shall prevail, unless explicitly stated otherwise in the Technical Specification.

____________________________