TECHNICAL SPECIFICATION

- DEFINITIONS AND ABBREVIATIONS

  - Client – UAB Kauno kogeneracinė jėgainė (KKJ).

  - Service Provider – an economic operator – a natural person, a private legal entity, a public legal entity, other organizations and their branches, or a group of such persons, with whom the Client enters into the Contract.

  - Contract – the agreement concluded between the Client and the Provider regarding the Object of Procurement.

  - DCS – Emerson Ovation DCS control system.

  - PWCS – Power and Water Cybersecurity Suite.

  - NIS2 – (Network and Information Security Directive 2) is a European Union (EU) cybersecurity directive aimed at ensuring a high and uniform level of cybersecurity across the EU.

  - SAT – Site acceptance test (acceptance testing of the object of procurement).

  - KVM – (Keyboard, Video, Mouse) A hardware (physical) device that allows multiple computers or servers to be controlled using a keyboard, mouse, and monitor.

  - Services – DCS system upgrade services.

  - Goods – materials / parts required for the provision of the Services.

  - Order – a a written document submitted to the Service Provider by text message or e-mail on the basis of the Agreement, specifying the scope of the Services to be ordered and the time limit for the provision of the Services.

- CHARACTERISTICS AND SCOPE OF THE OBJECT OF PROCUREMENT

  - DCS system upgrade to Emerson Ovation 4.0

  - Services and Goods quantities are provided in the table below.

Table 1 Quantities

| Pos. No. | Description | Unit of measure | Quantity |
| --- | --- | --- | --- |
| Workstations and monitors |  |  |  |
| 1. | Database Server - Dell PowerEdge Rackmount Server - Redundant Power Supply Units - Microsoft Windows Server 2025 | pcs. | 1 |
| 2. | Ovation Process Historian Server - Dell PowerEdge Rackmount Server - Redundant Power Supply Units - Microsoft Windows Server 2025 | pcs. | 1 |
| 3. | Operator / Eng Workstation - Dell Precision Rackmount - Dual Screen Capability - Microsoft Windows 11 IoT Enterprise LTSC 2019 Embedded license | pcs. | 5 |
| 4. | PWCS Virtualization Host - Dell PowerEdge Rackmount Server - Redundant Power Supply Units - Microsoft Windows Server 2025 | pcs. | 1 |
| 5. | PWCS Workstation - Dell Precision Rackmount Server - Redundant Power Supply Units - Microsoft Windows 11 IoT Enterprise | pcs. | 1 |
| 6. | PWCS NAS - Synology Rackstation | pcs. | 1 |
| Network equipment |  |  |  |
| 7. | Root Switch - CISCO 9200L | pcs. | 2 |
| 8. | Fan-out Switch - CISCO 9200L | pcs. | 2 |
| 9. | IP Traffic Switch - CISCO 9200L | pcs. | 1 |
| 10. | Router - CISCO 1120 | pcs. | 4 |
| 11. | PWCS Switch - CISCO 9200L | pcs. | 1 |
| 12. | PWCS Router - CISCO 1120 | pcs. | 1 |
| System software |  |  |  |
| 13. | Ovation Database Server Software license – upgrade Ovation Database Server Software for Master Database interface and management | pcs. | 1 |
| 14. | Ovation Engineering Tools Software license – upgrade Standard Ovation Engineering Tools (Developer Studio, Graphics Builder, Control Builder) | pcs. | 1 |
| 15. | Ovation Operator Tools Software license – upgrade Standard Ovation Operator Tools (Alarm List, Graphic Display, Trends, Point Info, etc.) | pcs. | 5 |
| 16. | Ovation Redundant Controller Software license – upgrade Ovation Controller System Software | pcs. | 7 |
| 17. | Ovation Process Historian license – upgrade Ovation Process Historian Software for archiving process point values, alarms, events and reports | pcs. | 1 |
| 18. | Ovation OPC UA Server Software license – upgrade OLE for Process Control (OPC) communication software | pcs. | 2 |
| 19. | Ovation OPC UA Client Software license – upgrade OLE for Process Control (OPC) communication software | pcs. | 2 |
| 20. | Ethernet Link Controller Modbus master license – upgrade Modbus TCP communication interface software | pcs. | 5 |
| 21. | Ethernet Link Protocol IEC 60870-5-101 | pcs. | 2 |
| 22. | Ethernet Link Protocol IEC 60870-5-104 | pcs. | 4 |
| 23. | Ethernet Link Protocol Modbus Master/Slave | pcs. | 4/4 |
| 24. | Ethernet Link Protocol IEC 61850 | pcs. | 2 |
| 25. | Global Performance Advisor license - upgrade | pcs. | 1 |
| 26. | Remote Desktop Services Device CAL - 5 pack | pcs. | 1 |
| 27. | SIS Configuration Tool | pcs. | 1 |
| Third party software |  |  |  |
| 28. | Windriver VxWorks Software license (Redundant Controller) – upgrade Ovation controller real time operating system | pcs. | 7 |
| 29. | SAP Crystal Reports license – upgrade Reporting system engine software | pcs. | 1 |
| PWCS Software |  |  |  |
| 30. | Microsoft Windows Server 2025 Standard License License for Virtual Machines operating system (1 license pack for 2 VMs) | pack | 1 |
| 31. | PWCS Dashboard McAfee ePolicy Orchestrator (ePO) – Unified console/dashboard for Patch Management, AntiVirus, Application Control and Device Control | pcs. | 1 |
| 32. | PWCS Anti-Virus McAfee Endpoint Security licenses with 1- year support | lot | 1 |
| 33. | PWCS Patch Management Autonomic ANSA Patch Manager licenses with 1-year support | lot | 1 |
| 34. | PWCS Application Control McAfee Application Control licenses with 1-year support | lot | 1 |
| 35. | PWCS System Backup & Recovery Management Server - upgrade Acronis Backup & Recovery Management Server | pcs. | 1 |
| 36. | Acronis Backup & Recovery Advanced Workstation - upgrade Licenses for workstation-class machines | pcs | 2 |
| 37. | Acronis Backup & Recovery Advanced Workstation - upgrade Licenses for workstation-class machines | pcs. | 5 |
| In-house engineering services |  |  |  |
| 38. | Engineering services: - Project management and planning; - System configuration and application software backup; - New workstations setup; - System configuration and application software restore on the new workstations; - System internal tests. | lot | 1 |
| On-site KKJ engineering services |  |  |  |
| 39. | Ovation on-site engineering services: - New workstations installation assistance and verification - Historical data transfer to new historian server - Startup and testing the system after upgrade - Site acceptance test (SAT) | days | 15 |
| 40. | PWCS on-site engineering services: - PWCS Startup and final integration with Ovation - Site acceptance test (SAT) | days | 10 |

Description of the object of procurement

  - DCS upgrade will cover replacement of workstations, network hardware as well as system software upgrade. Controller’s hardware, I/O and communication modules will be retained.

  - The scope of the Ovation Security Center upgrade covers hardware and system software upgrade to latest Power and Water Cybersecurity Suite.

  - An outage of 5 days is required to execute the Upgrade of Ovation (PWCS Upgrade does not require an outage)

  - The service provider will provide complete engineering services to upgrade the DCS and PWCS Systems including detailed project engineering, upgrade of hardware and system software, system testing, system start-up and ongoing support of the Kaunas CHP Power Plant.

  - Current system configuration:

    - Kaunas CHP Power Plant is currently at 3.6 software level and consist of the hardware listed in the following table.

Table 2 Current system configuration

| DROP ID | Type | Specification | HW Exchanged/ HW Maintained |
| --- | --- | --- | --- |
| 160 | Historian Server | Dell PowerEdge R740 | HW Exchanged |
| 200 | Database Server | Dell PowerEdge R740 | HW Exchanged |
| 211 | Operator Station | Dell Precision 7920 | HW Exchanged |
| 212 | Operator Station | Dell Precision 7920 | HW Exchanged |
| 213 | Operator Station | Dell Precision 7920 | HW Exchanged |
| 214 | Operator Station | Dell Precision 7920 | HW Exchanged |
| 215 | Operator Station | Dell Precision 7920 | HW Exchanged |
| 216 | Operator Station | Valueline VL2 PPC 3000 | Decommissioned |
| 1/51 | Redundant Controller | OCR1100 | HW Maintained |
| 2/52 | Redundant Controller | OCR1100 | HW Maintained |
| 3/53 | Redundant Controller | OCR1100 | HW Maintained |
| 4/54 | Redundant Controller | OCR1100 | HW Maintained |
| 5/55 | Redundant Controller | OCR1100 | HW Maintained |
| 6/56 | Redundant Controller | OCR1100 | HW Maintained |
| 7/57 | Redundant Controller | OCR1100 | HW Maintained |
| - | Ovation I/O Modules | Multiple types | HW Maintained |
| - | Ovation Communication Modules | Ethernet Link Controller | HW Maintained |
| - | Ovation Routers | Cisco ISR4321 x2 | HW Exchanged |
| - | Firewall Routers | Cisco ISR4321 x2 | HW Exchanged |
| - | Oavation Switches | Cisco 2690+ | HW Exchanged |

    - Kaunas CHP Power Plant is currently at 3.3 software level and consist of the hardware listed in the following table.

Table 3 Current Ovation Security Center configuration

| Item | Module | Type | HW Exchanged/ HW Maintained |
| --- | --- | --- | --- |
| A | PWCS Host | Dell PowerEdge Server | HW Exchanged |
| B | PWCS Firewall Router | Cisco ASA | HW Exchanged |
| C | PWCS Switch | Cisco WS- C3650 | HW Exchanged |
| D | PWCS Management Console (PWCS UI) | Dell Precision Workstation | HW Exchanged |
| E | PWCS Network Attached Storage | Synology | HW Exchanged |

  - Upgrade Scope:

    - DCS upgrade;

      - Main goal for the upgrade is to renew HMI hardware and keep Ovation software in supported status including controllers’ firmware update (if applicable).

      - Ovation controllers (OCR1100 CPU’s, IOIC’s, power supplies, I/O and communication modules) hardware need to be maintained.

      - Operator Station 216 will be decommissioned.

      - New workstations should be loaded with operating systems and new Ovation software before shipment to site. Site backup of existing Ovation configuration and application software should also be restored in advance to minimize system outage period.

      - During the KKJ outage new workstations and servers (without monitors) have to be installed in place of existing ones and connected using existing KVM (if applicable), power and network cables. Historical data has to be retained and transferred to the new historian server.

    - PWCS upgrade;

      - Only PWCS 3.5 hardware will be maintained.

      - PWCS 3.5 software components will be updated to PWCS 3.6 versions using existing or upgraded licenses.

  - Engineering services:

    - In-house engineering services include all necessary preparations of the system upgrade and implementation before arriving to site as described in Table 3 row 38.

    - On-Site engineering services should consist of:

      - Amount of 15 (fifteen) work-days of field-service for the DCS installation verification, DCS start-up and basic DCS (HW & system SW) testing and all the Project Coordination.

      - Amount of 10 (ten) work-days for PWCS start-up, integration with Ovation, basic PWCS functionality testing and all the Project Coordination.

  - All necessary hardware equipment needed for DCS Ovation system upgrade should strictly be exchanged with compliance according Emerson requirements, suggestions and instructions, since KKJ power plant operates on  Emerson Ovation DCS system.

  - Any offered hardware and/or software which does not fall under Emmerson approved list should get an official Emerson acceptance document regarding compatibility, reliability with Emerson Ovation and PCWS systems.

  - Upgraded Emerson Ovation and PWCS systems should meet NIS2 requirements.

- PLACE, PROCEDURE AND TERMS OF SERVICE PROVISION

  - The Services shall be provided within 2 (two) years from the date of signing the Contract at the latest. Place of provision: Jėgainės g. 6, Biruliškių k., Karmėlavos sen., LT-54469, Kaunas district, during the Client’s business hours (I–IV 7:30 – 16:30, V 7:30 – 15:15).

  - The following documents shall be submitted together with the services provided:

    - A deed of acceptance – transfer of the Services and/or Goods;

    - A Report of implemented upgrade;

    - Ovation and PWCS user guides;

    - System architecture and network design drawings – update;

    - Manufacturer documentation for delivered hardware.

    - SAT protocols

  - Payments shall be executed in consideration of the project implementation milestones; the milestones shall be implemented in accordance with the project schedule agreed upon between the Service Provider and the Client. Settlements shall be made in two stages, upon signing the completion act for each respective stage:

    - STAGE 1 completed – Hardware and software specified in items 1–29, 38, and 39 of Table No. 1 have been installed/deployed. Upon signing the completion act for STAGE 1, the Client undertakes to pay 50% of the Services price specified in the Contract, according to the invoice provided by the Service Provider.

    - STAGE 2 completed – Software specified in items 30–37 and 40 of Table No. 1 has been installed/deployed. Upon signing the completion act for STAGE 2, the Client undertakes to pay the remaining 50% of the Services price specified in the Contract, according to the invoice provided by the Service Provider.

  - The Client takes responsibility of placing an order on year 2027 in January in order for the provider to meet delivery times to successfuly implement STAGE 1 (point 3.6.1) upgrade during plant outage.

  - The project schedule wit milestones will be agreed between Service provider and Client within 2 months after sending official order of a DCS system Upgrade to the Service provider.

  - The implementation of project in Kaunas CHP shall be devided into two stages:

    - STAGE 1 – Ovation upgrade. It should be done during plant outage in 15 man days. Preliminary date 2027 August – September

      - New workstations installation assistance and verification;

      - Historical data transfer to new historian server

      - Startup and testing the system after upgrade;

      - Site acceptance test (SAT).

    - STAGE 2 – PWCS upgrade. It should be done in 10 man days after STAGE 1 completion. The implementation of STAGE 2 ahould not be delayed more than  21 (twenty one) calendar days.

      - PWCS Startup and final integration with Ovation;

      - Site acceptance test (SAT).

    - Conditions for postponement:

      - On the Client's initiative: Since the PWCS upgrade can be performed while the power plant is operational, the Client shall have the right to reasonably postpone the start of this stage for up to 21 days (the exact postponement period shall be agreed upon with the Service Provider), if the operational state of the power plant, network stability requirements, or other dispatching restrictions do not allow for the safe execution of integration works at that time. The Client shall notify the Service Provider thereof at least 5 (five) business days in advance.

      - On the Service Provider's initiative: The Service Provider may request to postpone STAGE 2 works (for no longer than the 21 calendar days provided for in Clause 3.6.2) solely due to objective technical reasons that became apparent during STAGE 1 (e.g., detected incompatibilities requiring additional software code modification by the manufacturer). This request must be reasoned, submitted in writing, and approved by the Client.

  - Invoices will be paid in 30 days from the date of submission of the invoice to the Client.

- OTHER REQUIREMENTS

  - The aspects which do not fall under service provider scope:

    - Any Installation services such as: workstations replacement, cable connections, extraction/disconnection of old servers/workstations and connection/positioning of new ones in the cabinet. All these activities are supposed to be performed by Client personnel (The service provider will provide only Supervision);

    - Any modifications to the control application software;

    - Third party systems upgrade, integration and/or programming;

    - Large screens delivery.

  - The Client shall provide all necessary documentation for the provider of the existing system including DCS network layout, current configuration of system and etc.

  - The Service provider shall provide no less than a 12-month warranty for the Services from end date of performing Services and signing a completion of Services protocol.

  - The equipment provided should have a manufacturer’s warranty for no less than 1 year.