TECHNICAL SPECIFICATION

- DEFINITIONS AND ABBREVIATIONS

1.1. Customer - AB “Amber Grid”.

1.2. Supplier - an economic entity - natural person, private legal person, public legal person, other organisations and their subdivisions or a group of such persons, with which the Customer enters into an Agreement.

1.3. Agreement - an agreement concluded between the Supplier and the Buyer in relation to the Procurement object.

1.4. Goods with services - hot tapping/drilling equipment or set of equipment for drilling holes from DN50 to DN400 in existing high pressure gas pipelines with a pressure of 5,4 MPa, with additional equipment and components.

- THE PROCUREMENT OBJECT, THE QUANTITIES (VOLUMES) AND A DETAILED DESCRIPTION OF THE PROCUREMENT OBJECT

2.1. Procurement object - hot tapping/drilling equipment or set of equipment for drilling holes from DN50 to DN400 in existing high pressure gas pipelines with a pressure of 5,4 MPa, with additional equipment and components.

- Table 1. Names and quantities of Goods to be purchased

| No. | Name | Description | Quantity | Note |
| --- | --- | --- | --- | --- |
| 1. | Drilling equipment for drilling holes in existing high-pressure gas pipelines (5,4 MPa) DN80-DN400 and for the blocking of a functioning pipeline • Basic drilling equipment and technical requirements: • Drilling range from DN80 to DN400 (3" to 16") • Dual hydraulic actuator with two (2) motors, capable of running in series or parallel. A lever is used to control the operating system; • Hand crank - a handle that allows manual insertion and/or removal of the drilling machine shaft (or equivalent solution); • Shaft with an inch scale of the measuring system, which allows the position of the drilling machine shaft to be read and the drilling machine shaft to be connected to the cutter holder and the bail (or equivalent); • Shaft pusher - a device to connect the shaft of the equipment to the plug holder in the event of a leak in the plug valve structure (or equivalent); • Round metal RTJ sealing ring - a gasket that seals the connection between the drilling equipment and the drilling/connection adapter; • The shaft of the equipment, designed for sealed operation (drilling). Connection to tools with self-locking tapered socket. • The shaft of the equipment for performing/connecting the sealing operation (placing of the plug); • Possibility to upgrade the equipment in the future and extend the drilling range up to DN500 by adding additional elements and accessories. • The drill shaft stroke of the drilling equipment shall be at least 1750 mm. • Weight of the equipment up to 300 kg. • Length of the equipment up to 2500 mm • Robust and durable drill shaft design for low vibration and wear resistance. |  | 1 pcs. |  |
| 1.1. | Additional equipment for the drilling machine for drilling holes in DN80-DN400 diameter in high-pressure (5,4 MPa) gas pipelines and for blocking the pipeline. |  |  |  |
| 1.1.1 | The drive unit - a diesel hydraulic unit with an electric starting system. Structure with transport frame, lifting eyelets. The equipment must be suitable for transport by forklift and jib crane. Includes hydraulic hoses to connect the drilling equipment and the drive unit, with 1", 3/4" and 3/8" hose diameters and a minimum length of 15 metres, with quick couplings at the ends compatible with the Contracting Party's range of equipment. |  | 1 set |  |
| 1.1.1.1 | Cutter holders for diameters from 3" to 16" |  | 1 pcs. |  |
| 1.1.1.2 | LOR-type plug holder for diameters from DN100 (4") to DN400 (16") |  | 1 pcs. |  |
| 1.1.1.3 | Linestop cutter 4"-100 mm, |  | 2 pcs. |  |
| 1.1.1.4 | Linestop cutter 6"-150 mm |  | 2 pcs. |  |
| 1.1.1.5 | Linestop cutter 8"-198 mm |  | 2 pcs. |  |
| 1.1.1.6 | Linestop cutter 10"-248 mm |  | 2 pcs. |  |
| 1.1.1.7 | Linestop cutter 12"-298 mm |  | 2 pcs. |  |
| 1.1.1.8 | Linestop cutter 14"-332 mm |  | 2 pcs. |  |
| 1.1.1.9 | Linestop cutter 16" -383 mm for pipe OD-406 mm |  | 2 pcs. |  |
| 1.1.1.10 | Linestop cutter 16" for pipe OD-426 mm |  | 2 pcs. |  |
| 1.1.1.11 | Incising cutter 4" -87mm |  | 2 pcs. |  |
| 1.1.1.12 | Incising cutter 6"-139 mm |  | 2 pcs. |  |
| 1.1.1.13 | Incising cutter 8" -186mm |  | 2 pcs. |  |
| 1.1.1.14 | Incising cutter 10" -241mm |  | 2 pcs. |  |
| 1.1.1.15 | Incising cutter 12" -292mm |  | 2 pcs. |  |
| 1.1.1.16 | Incising cutter 14" -324mm |  | 2 pcs. |  |
| 1.1.1.17 | Incising cutter 16"-373 mm for pipe OD-406 mm |  | 2 pcs. |  |
| 1.1.1.18 | Incising cutter 16" for pipe OD-426 mm |  | 2 pcs. |  |
| 1.1.1.19 | "Hottap" adapter 4" with 3/8" and 1" NPT connectors |  | 2 pcs. |  |
| 1.1.1.20 | "Hottap" adapter 6" with 3/8" and 1" NPT connectors |  | 2 pcs. |  |
| 1.1.1.21 | "Hottap" adapter 8" with 3/8" and 2" NPT connectors |  | 2 pcs. |  |
| 1.1.1.22 | "Hottap" adapter 10" with 3/8" and 2" NPT connectors |  | 2 pcs. |  |
| 1.1.1.23 | "Hottap" adapter 12" - 323,9 mm with 3/8" and 2" NPT connectors |  | 2 pcs. |  |
| 1.1.1.24 | "Hottap" adapter 12" - 325 mm with 3/8" and 2" NPT connectors |  | 2 pcs. |  |
| 1.1.1.25 | "Hottap" adapter 14" with 3/8" and 2" NPT connectors |  | 2 pcs. |  |
| 1.1.1.26 | "Hottap" adapter 16" - 406 mm with 3/8" and 2" NPT connectors |  | 2 pcs. |  |
| 1.1.1.27 | "Hottap" adapter 16" - 426 mm with 3/8" and 2" NPT connectors |  | 2 pcs. |  |
| 1.1.1.28 | 4" guiding drill |  | 4 pcs. |  |
| 1.1.1.29 | 6" guiding drill |  | 4 pcs. |  |
| 1.1.1.30 | 8" guiding drill |  | 4 pcs. |  |
| 1.1.1.31 | 10" b guiding drill |  | 4 pcs. |  |
| 1.1.1.32 | 14" guiding drill |  | 4 pcs. |  |
| 1.1.1.33 | 16" guiding drill- 406 mm |  | 4 pcs. |  |
| 1.1.1.34 | Small machine pneumatic drive motor |  | 1 pcs. |  |
| 2. | Drilling equipment for drilling holes in existing high-pressure gas pipelines (5.4 MPa) DN50-DN150 Basic drilling machine equipment: • Hand crank - a handle that can be used to turn the shaft of the drilling equipment (or equivalent solution); • Hood - a component that allows the rotation of the machine shaft to be blocked and allows the installation and/or removal of the plug (or equivalent solution); • The body of the equipment with the option of a pressure relief valve to release pressure from the equipment; • Electric screwdriver for unscrewing the shaft seal assembly of the Equipment (or equivalent solution). • Weight of the equipment up to 20 kg • The drill shaft stroke of the drilling equipment shall be at least 760 mm • Steel shipping container • Abrasion, corrosion and scratch resistant surface. |  | 1 pcs. |  |
| 2.1. | Additional equipment for drilling holes for drilling holes of diameters DN50-DN150 and plugging holes in high pressure gas pipelines (5.4 MPa) DN50-DN150 |  |  |  |
| 2.1.1 | Plug holder for diameters DN50 to DN100 |  | 1 pcs. |  |
| 2.1.2 | Cutter holder for diameters DN50-DN150 “size-on-size” |  | 2 sets |  |
| 2.1.3 | Cutter holder for diameters DN50-DN150 “non size-on-size” |  | 2 sets |  |
| 2.1.4 | Cutter for hole d-98,4 mm (3-7/8") |  | 2 pcs. |  |
| 2.1.5 | Drill bit d-36,5 mm (1-7/16") |  | 2 pcs. |  |
| 2.1.6 | Thread adapter DN50 with 2" NPT tapered male thread |  | 2 pcs. |  |
| 2.1.7 | Threaded adapter DN80 with 2" and 3" NPT tapered male threads |  | 2 pcs. |  |
| 2.1.8 | Flange adapter DN80 - (3") ANSI class 600 |  | 1 pcs. |  |
| 2.1.9 | Flange adapter DN100 - (4") ANSI class 600 |  | 1 pcs. |  |
| 3. | GENERAL REQUIREMENTS FOR EQUIPMENT 1 AND 2 (SET) |  |  |  |
| 3.1. | Hydraulic cylinders for shutting off pipelines DN100-DN400 diameter at a pressure of 5,4 MPa |  |  |  |
| 3.1.1 | Hydraulic “linestop” drive for 4"-12", used with stopper housings and heads, for lowering the plug into the pipeline and shutting off the flow; after the work is done, removing the plug and thus fully restoring the flow at a pressure of 5,4 MPa. |  | 2 sets |  |
| 3.1.2 | Hydraulic “linestop” drive for 14"-20", used with stopper housings and heads, for lowering the plug into the pipeline and shutting off the flow; after the work is done, removing the plug and thus fully restoring the flow at a pressure of 5,4 MPa. |  | 2 sets |  |
| 4. | Closing housings, heads and seals |  |  |  |
| 4.1. | Closing housing DN100-4" ANSI 600 class with 3/8" and 1" NPT female threaded connectors |  | 2 pcs. |  |
| 4.2. | Closing housing DN150-6" ANSI 600 class with 3/8" and 1" NPT female threaded connectors |  | 2 pcs. |  |
| 4.3. | Closing housing DN200-8" ANSI 600 class with 3/8" and 2" NPT female threaded connectors |  | 2 pcs. |  |
| 4.4. | Closing housing DN300-12" ANSI 600 class with 3/8" and 2" NPT female threaded connectors |  | 2 pcs. |  |
| 4.5. | Closing housing DN350-14" ANSI 600 class, OD-406mm, with 3/8" and 2" NPT female threaded connectors |  | 2 pcs. |  |
| 4.6. | Closing housing DN350-16" ANSI 600 class, OD-406mm, with 3/8" and 2" NPT female threaded connectors |  | 2 pcs. |  |
| 4.7. | Closing housing DN350-16" ANSI 600 class, OD-426mm, with 3/8" and 2" NPT female threaded connectors |  | 2 pcs. |  |
| 4.8. | Closing head DN100 ANSI 600 class with nozzle kit for pipes ID DN100 - 4" |  | 2 pcs. |  |
| 4.9. | Closing head DN150 ANSI 600 class with nozzle kit for pipes ID DN150 - 6" |  | 2 pcs. |  |
| 4.10 | Closing head DN200 ANSI 600 class with nozzle kit for pipes ID DN200 - 8" |  | 2 pcs. |  |
| 4.11 | Closing head DN300 ANSI 600 class with nozzle kit for pipes ID DN300 - 12" |  | 2 pcs. |  |
| 4.12 | Closing head DN350 ANSI 600 class with nozzle kit for pipes ID DN350 - 14" |  | 2 pcs. |  |
| 4.13 | Closing head DN400 OD-406 mm ANSI class 600, with nozzle kit, for pipes ID DN350-16" |  | 2 pcs. |  |
| 4.14 | Closing head DN400 OD-426 mm ANSI class 600, with nozzle kit, for pipes ID DN350-16" |  | 2 pcs. |  |
| 4.15 | 4" sealing elements |  | 4 pcs. |  |
| 4.16 | 6" sealing elements |  | 4 pcs. |  |
| 4.17 | 8" sealing elements |  | 4 pcs. |  |
| 4,18 | 10" sealing elements |  | 4 pcs. |  |
| 4.20 | 12" sealing elements |  | 4 pcs. |  |
| 4.21 | 14" sealing elements |  | 4 pcs. |  |
| 4.22 | 16" sealing elements |  | 4 pcs. |  |
| 4.23 | 17" Sealing elements, for pipe OD 426 mm |  | 4 pcs. |  |
| 5. | Sandwich valves from DN100-4" to DN400-16" ANSI 600 class |  |  |  |
| 5.1. | Sandwich valve DN100 - 4" ANSI 600 class |  | 2 pcs. |  |
| 5.2. | Sandwich valve DN150 - 6" ANSI 600 class |  | 2 pcs. |  |
| 5.3. | Sandwich valve DN200 - 8" ANSI 600 class |  | 2 pcs. |  |
| 5.4. | Sandwich valve DN300 - 12" ANSI 600 class |  | 2 pcs. |  |
| 5.5. | Sandwich valve DN350 - 14" ANSI 600 class |  | 2 pcs. |  |
| 5.6. | Sandwich valve DN400 - 16" ANSI Class 600 for pipes OD-406 mm |  | 2 pcs. |  |
| 5.7 | Sandwich valve DN400 - 16" ANSI 600 class, for pipes OD-426 mm |  | 2 pcs. |  |
| 6. | Theoretical and practical training in the operation and maintenance of the equipment, followed by training by the supplier in the periodic maintenance of the equipment. The training must be provided in Lithuanian. |  | 6 people |  |

1)  DRILLING EQUIPMENT OR SET OF EQUIPMENT FOR HOLES DN50-DN400.  The equipment is designed to hermetically penetrate an operating pipeline at a working pressure of 5,4 MPa. Drill holes in gas pipelines with cutters and perform plugging and unplugging operations. Fitted with brackets suitable for LOR-type plugs (interlocked by segments protruding from the flange of the fitting). The design of the equipment must ensure a smooth connection between the drill shaft, the cutters and the plug holders.

The equipment is designed to hermetically penetrate an operating pipeline at a working pressure of 5,4 MPa using drills and cutters, and to carry out the operations of inserting and removing plugs. Fitted with holders suitable for LOR-type plugs (interlocking segments protruding from the flange of the fitting). The design of the equipment must ensure a smooth connection between the drill shaft, cutters and drill bits. Ensure that the holes can be drilled using a suitable pneumatic or hydraulic motor.

3) PLUG HOLDER - the design of the holder shall be such that the shaft of the drilling equipment can be connected to the sealing plug; a type of plug adapter adapted for connection by means of wedges coming out of the connecting flange.

4)  CUTTER HOLDER - a device that allows the drilling machine shaft to be connected to the cutter and the guide drill.

5) DILLING AND PLUG ADAPTER - a device allowing the drilling equipment to be safely connected to a shut-off valve for the drilling of the gas pipeline with a cutter and for the installation and removal of LOR plugs. The adaptor shall have a gas outlet, a pressure equalisation connection and transport handles. Adapter with flange connector for connection to the shut-off valve

6)  THREAD ADAPTER - adapter for connecting the drilling equipment to a threaded valve with NPT taper thread.

7) FLANGE ADAPTER - a flange adapter for connecting the drilling equipment to a closing valve

8) HYDRAULIC CILINDERS - a device that works in conjunction with the drive unit. The design of the cylinder (piston) shall allow (in combination with the closing head) for lowering the plug head into the pipeline, shutting off the flow; removing the plug head after the work has been carried out, and restoring the flow completely at a pressure of 5,4 MPa.

9) CLOSING BODY - a device allowing the repeated and safe connection of a hydraulic cylinder to the closing valve to allow the assembly and disassembly of the closing head in the pipeline at a working pressure of 5,4 MPa. The design of the casing shall permit complete withdrawal of the closing head, which shall be fitted with a sealing element to stop the flow of gas. The head shall be equipped with a gas outlet, a pressure equalisation outlet and transport handles. The connection between the housing and the closing valve - flanged.

10) CLOSING HEAD - The design shall provide effective passage through the opening cut in the pipeline and shall be in a position to stop the flow and ensure the tightness of the closing device in the pipeline. The head shall operate at a working pressure of 5,4 MPa. The head shall be capable of being fitted with a set of rings and closing couplings or an equivalent system

11) CLOSING HEAD SEALING KIT - A special shut-off head component that allows the flow to be shut off at a given internal diameter of the pipeline (or an equivalent system that allows the diameter of the shut-off head to be adjusted to the internal diameter of the pipe).

12) SANDWICH VALVE - a device used to isolate device and equipment from a pressurised pipeline. The design of the closing valve shall allow for the safe installation of the drilling machine connections, disconnection, plugging and shut-off of the pipeline at a pressure of 5,4 MPa. The parameters of the closing valve must allow these functions to be performed repeatedly. The closing valve is manually operated.

2.    General requirements

2.1.   The Goods purchased must be brand new and must be delivered in the original unopened factory packaging. Factory refurbished ("renewed"/"refurbished"/"remarked") Goods are not suitable.

2.2.  The procurement object must have been recently manufactured (date of manufacture no more than 12 months before the date of delivery).

2.4. The procurement object must bear a manufacturer's (name) plate and have an identification/serial number or mark allowing the object to be attributed to a specific quality document.

2.5.  The drilling equipment must be covered by a 60-month warranty and the specified components by a 24-month warranty.

2.6.  Drilling equipment and accessories must be made from components that will be available on the market for at least 15 years.

2.7.  The Customer shall not allow the use of additional fittings (adaptors) between the drilling equipment and the adaptor, nor of the hydraulic cylinder and the casing of the closing head, which limit the operating range of the equipment.

3.    Requirements for the procurement object

3.1.  Drilling equipment or set of equipment for drilling and plugging holes of DN50-DN400 diameter in existing gas pipelines at a working pressure of 5,4 MPa including accessories.

3.1.1. The equipment is suitable for repeated and safe drilling in active gas pipelines with a maximum working pressure of 5.4 MPa. When fitted with the appropriate cutters, the machine can drill holes in active gas pipelines from 61.9 mm (2-7/16") to 426 mm (16") in diameter.

3.1.2. The equipment shall allow for the reinsertion and safe removal of LOR-type plugs using appropriate holders, connectors and ports. Dealing with plugs in flanges and ports with diameters from DN50 to DN400.

3.1.3. The drilling equipment shall be equipped with a hydraulic drive, hand crank, measuring rod, measuring rod pusher, and seals between the equipment and the drilling adaptors as standard.

3.1.4.  The drilling equipment is additionally equipped with the items listed in section 2 of the table of the object of the order.

3.1.5.  The drill shaft of the equipment is suitable for the installation of cutter holders and plug holders with a minimum length of 1750mm (min. 70"). 70 Shaft end with self-locking inner cone, allowing the attachment of cutter and plug holders compatible with the Customer's product range.

3.1.6. Drilling machines with handles for carrying during assembly or disassembly, depending on the job at hand.

3.1.7. The drive unit shall be compatible with the operating parameters and hydraulic cylinders and equipment of the drilling equipment owned by the Contracting Party.

3.1.8. The drive unit is equipped with a diesel engine with electric start. Switching to operating mode from the dashboard with the ignition key.

3.1.9. Drive unit with transport handles and lifting eyelets for crane transport.

3.1.10. A drill and plug fitting adapter with a connecting flange to ANSI Class 600 with RF faces to ASME B16.5 (or equivalent) shall provide a secure connection between the drill equipment and the seal ring. The adapter shall allow for the assembly/disassembly of LOR-type plugs, shall have appropriate openings and fixed transport handles.

3.2. Drilling equipment for drilling and plugging holes of DN50-DN150 diameter in existing gas pipelines at a working pressure of 54 MPa including accessories.

3.2.1. The equipment is designed for repeated and safe drilling in active gas pipelines at a maximum working pressure of 8.4 MPa. The equipment can drill holes in existing gas pipelines from 12.7 mm (1/2") to 150 mm (6") in diameter when fitted with the appropriate drill bits or cutters. The equipment is manually operated with the option of connecting a pneumatic or hydraulic motor

3.2.2. The equipment shall provide for the safe multiple insertion and removal of LOR-type plugs using appropriate connectors.

3.2.3. The basic drilling machine shall be equipped with a manual mechanism, a handle for levelling the machine and rotating and locking the shaft, and a wrench for installing the shaft sealing pack. The body of the equipment shall be able to accommodate a valve to release pressure from the equipment.

3.2.4. The drill shaft of the equipment shall be suitable for the installation of 760 mm (30") cutters, cutter holders and drill bits.

3.3.    Hydraulic cylinder for shutting off DN100-DN400 gas pipelines at a pressure of 5.4 MPa.

3.3.1. A hydraulic cylinder (piston) working with a hydraulic power unit. A cylinder design that allows the closing head to be efficiently lowered into the pipeline for the closing operation. The cylinder shall be fitted with transport and mounting lugs.

3.3.2. The hydraulic cylinder shall have a visible measuring scale and an inspection port at the bottom of the cylinder to read the position of the closing head. Control valves at the bottom of the cylinder with hydraulic connections to connect the power unit.

3.3.3. The hydraulic cylinder must be fitted with a safety valve.

3.3.4. The hydraulic cylinder shall be capable of adjusting the stroke speed.

3.4.    Delivery of housing for closing heads

3.4.1. The closing head housing shall provide for multiple and safe connection of the hydraulic cylinder with the closing head to the closing points with the closing valve to stop and restore the flow of gas in the pipe.

3.4.2. The design of the closing head housing shall ensure that the closing end can be fully inserted into the housing.

3.4.3.   The closing head housing is constructed according to ANSI Class 600 with a connecting flange with RF surface according to ASME 16.5. (or equivalent)

3.4.4.   The head housing shall have a 3/8" (1" NPT female thread) gas outlet and a 2" (2" NPT female thread) outlet.

3.5.       Sandwich valve delivery ANSI Class 600.

3.5.1.   Sandwich closing valve, ANSI Class 600, with fittings, ports, drilling and closing adapters manufactured according to ASME B16.5.

(or equivalent).

3.5.2.   Sandwich valve operated by manual gear.

3.5.3.   Reversible design allowing installation in either direction.

3.5.4.   A gate valve with an internal bypass for filling with gas.

3.5.5.  The kit shall include mounting screws for installation with connectors, drill adapter or closing adapter in accordance with ASME BI 6.5 (or equivalent standard)

3.5.6.   Each valve shall have protective covers to cover the mounting screws during transport and storage (2 covers per valve).

3.5.7. The gate valve shall have at least 4 removable transport handles, two on each of the longer sides of the valve.  Holes for transport handles should be provided in each main structural element of the gate valve (top plate, middle plate, bottom plate), two on each longer side of the gate valve, to allow for the provision of transport handles for the individual components of the gate valve during the inspection work.

3.6.   Theoretical and practical training in Lithuanian; final test of knowledge with a certificate entitling a person to work on, assess and maintain the equipment. The training must be conducted by qualified instructors from the equipment manufacturer and must take place in a training facility with a properly equipped training pipeline. Each participant must be given the opportunity to receive practical training in working with equipment under pipeline pressure.

Minimum theoretical and practical training:

•   calculations for drilling and plugging processes;

•   measurements and preparatory work before work starts;

•  construction of device and equipment;

•   principles of device and equipment operation;

•   health and safety rules for working with machinery and equipment;

•  maintenance of devices and equipment;

•   training in the drilling process at the training centre,

•   the plugging process is taught in a training centre where a mock pipeline with a set of fittings and ports is installed.

•   The authority of the Customer's employees to carry out maintenance on the equipment. Note: Training must be provided before the delivery date of the equipment.

4.   Main operating parameters

4.1.   Maximum working pressure of gas pipelines: 5,4 MPa

4.2.   Ambient temperature: - 35 °C ÷ + 50 °C

4.3.   Gas temperature: - 10 °C ÷ + 50 °C

5. Delivery of the procurement object and submission of the Documents

5.1. The Goods must be accompanied by a detailed instruction manual (in Lithuanian or English);

5.2. Technical safety verification document;

5.3. Declaration of conformity;

5.4. Certificates for components;

5.5. Results of non-destructive testing;

5.6. Separate documents (technical drawings) shall be provided for each fitting after manufacture. Common documentation must be provided for connectors and nozzles, grouped into a range;

5.7. Documentation shall be provided for individual components to be ordered, such as bolts, nuts, washers and gaskets, confirming their conformity with this Description of the Object of the Order and the applicable standards;

5.8. Each material ordered must be clearly marked (e.g. engraved) by the manufacturer with a nameplate or an identifiable number or mark to link the range to a specific quality document.

5.9. Technical manufacturing documents;

5.10.   Acceptance of the procurement object will take place on a date agreed between the parties at the place of delivery, together with the relevant documents referred to in the Description of the object of the Agreement.

5.11. The Supplier shall notify the Customer's representative electronically at least 5 days in advance of the readiness for delivery and of the chosen delivery location. Failure to notify shall relieve the Customer of its obligation to accept the object of the Agreement.

5.12.   The Customer reserves the right to assess the conformity of the object of the Agreement with the requirements set out in the Proposal, the Technical Task, the Description of the Object of the Agreement and the Agreement at a location specified by the Supplier at the Supplier's manufacturing site before delivery of the object of the Agreement to the delivery site. Following the initial assessment, a preliminary inspection protocol will be drawn up. Preliminary protocol shall not constitute a basis for invoicing for the object of the Agreement and shall not constitute a basis for any other claims against the Customer. Signature of the preliminary inspection protocol does not constitute acceptance of the object of the Agreement.

5.13.  The Supplier shall deliver the object of the Agreement by its own means, at its own expense and risk, to the place of delivery specified by the Customer. The Supplier shall be responsible for selecting the appropriate vehicle and the appropriate route, taking into account in particular any traffic constraints arising from national or local legislation.

5.14. The Supplier shall properly pack and protect the object of the Agreement during transport to ensure that it is delivered to the Customer in good condition. The Supplier shall be liable for any damage caused during packing, transport and unloading.

5.15.  In the event of defects which impair the value or usefulness of the object of the Agreement for the purpose specified in the Agreement, the Supplier undertakes to compensate the Customer for the reasonable loss.

5.16.  If any defects (including qualitative or quantitative defects) are found upon acceptance of the object of the Agreement, the Customer shall have the right to refuse to accept the object of the Agreement or to accept the defective part of the object of the Agreement delivered. Defects which are grounds for refusal to accept part or all of the Agreement shall be recorded in the Acceptance protocol.

5.17.  Acceptance of the object of the Agreement will be confirmed by a Protocol of Acceptance of the Object of the Agreement signed by authorised representatives of both Parties.

5.18.  After the Customer has signed the protocol of acceptance with comments, the contractor has the right to reply to the Customer's comments within 5 working days.

5.19.  Notwithstanding the circumstances referred to in clause 7.6, in the event of comments, the Customer may also set a new one-off deadline within which the Supplier must deliver the object of the Agreement without defects. If the Supplier meets the specified additional delivery date, the contractual penalties for the relevant part of the object of the Agreement shall not apply. In the event of non-compliance with this additional delivery date, the contractual penalties will be calculated for the delay from the original due date. The acceptance procedure shall be repeated (without the possibility of an additional time limit) for the object of the Agreement which has been rejected by the Customer with observations in accordance with the provisions of this paragraph.

5.20.  Acceptance of the object of the Agreement without comments shall not relieve the Supplier of liability for latent defects, which shall be notified to the Supplier by the Customer without delay.

5.21.  If, at the time of acceptance of the object of the Agreement at the place of delivery, there is a dispute as to any defects in the object of the Agreement, the Parties shall appoint an acceptance committee. The acceptance committee shall consist of 4 (four) persons, two appointed by the Customer and two by the Supplier. If the work of the acceptance committee does not lead to a unanimous conclusion, the Parties shall appoint an independent expert. The costs of the expert's investigation shall be borne by the Party to whose disadvantage the conclusions of the said investigation are drawn. The results of the investigation, including its costs, will be included in a report prepared by the expert and signed by the Parties. If the acceptance committee or the independent expert confirms that the object of the Agreement is defective, the time spent by the acceptance committee or the independent expert shall be qualified by the Parties as a delay in the performance of the Agreement attributable to the Contractor.

5.22.  Having adopted a position according to clause 7.9, the Parties shall proceed in accordance with the provisions of this clause with respect to the acceptance of the object of the Agreement.

5.23.  At the Customer's request, all or part of the object of the Agreement shall be received at the Supplier's premises or at the place of storage or manufacture of the object of the Agreement.

5.24.  Upon signature by the Customer of the Protocol of Acceptance of the Object of the Agreement, the ownership of the object of the Agreement, to which the Customer has not objected, shall pass to the Customer. As from that date, the Customer shall assume the obligations and risk of accidental loss or damage to the object of the Agreement.

5.25.  6.15. The Customer shall not be liable for the risk of loss, damage or destruction of the object of the Agreement left by the Supplier and not collected by the Customer in the event of a refusal to take delivery or in the cases referred to in clauses 7.4 or 7.14.

5.26.  If the Supplier delivers the object of the Agreement by courier, the Customer shall acknowledge receipt of delivery in the presence of the courier. Within 5 working days of receipt of delivery, the Customer shall inspect the object of the Agreement in terms of quantity and quality, confirming conformity or notifying defects in the transfer-acceptance protocol. The Supplier's liability to the Customer shall not be limited by the terms of the Supplier's cooperation with the entities involved in the organisation and delivery of the Agreement.

6.     EU origin

The Supplier declares and agrees that, in submitting a proposal, the  Procurement object will be sourced from Member States of the European Union or countries with which the European Community has concluded agreements on equal treatment for businessmen, and that its share of the value of the Procurement object will exceed 50%.

7.     Environmental protection

9.1.   The Contractor is legally and financially responsible:

9.1.1. for damage caused to the environment as a result of activities related to the provision of the object of the Agreement;

9.1.2. for ensuring that each of its subcontractors complies with applicable environmental laws.

9.2.   The Supplier is required to:

9.2.1. report and prevent incidents affecting the environment;

9.2.2. appropriate measures must be in place to prevent the spread of pollution;

9.2.3. inform the Customer of events affecting the environment during the course of the provision of the object of the Agreement;

8.   Equivalent solutions

8.1. The object of the Agreement shall be described by standards, approvals, technical specifications or reference systems. The Customer shall allow solutions equivalent to those described. A Supplier seeking to provide an object of the Agreement may rely on equivalent solutions described by the Customer, but must demonstrate that its proposed object complies with the requirements specified by the Customer.

8.2. If the Agreement or any document of the terms of reference refers to any trademark, patent or certificate of origin, the Supplier should be deemed to have provided such a description by referring to the type and to authorise the use of materials whose equivalent technical characteristics are not inferior to those indicated under the term "type".

8.3. The goods must be delivered within 9 months of the conclusion of the agreement, to: Gudelių str. 49, Vilnius, Lithuania.

9. Additional elements of the hot cutting/drilling equipment to be procured.

- Table 2. Names and quantities of Goods to be procured

| No. | Description | Quantity | Note |
| --- | --- | --- | --- |
| 1 | Bypass flange DN100 ANSI600 with LOR plug and BF fitting | 11 | Part 1 - Flanges |
| 2 | Bypass flange DN150 ANSI600 with LOR plug and BF fitting | 12 |  |
| 3 | Bypass flange DN200 ANSI600 with LOR plug and BF fitting | 8 |  |
| 4 | Bypass flange DN250 ANSI600 with LOR plug and BF fitting | 6 |  |
| 5 | Bypass flange DN300 ANSI600 with LOR plug and BF fitting | 4 |  |
| 6 | Bypass flange DN400 ANSI600 with LOR plug and BF fitting | 4 |  |
| 7 | Threaded ventilation connector DN50 | 40 | Part 2 - Connectors |
| 8 | Threaded ventilation connector DN80 | 30 |  |
| 9 | Cylinder connector DN80 ANSI600 without plug with BF fitting | 5 |  |
| 10 | Balloon connector DN100 ANSI600 without plug with BF fitting | 4 |  |
| 11 | Cylinder connector DN150 ANSI600 without plug with BF fitting | 3 |  |
| 12 | Cylinder connector DN200 ANSI600 without plug with BF fitting | 4 |  |
| 13 | Cylinder connector LOR DN100 ANSI600 weldable with LOR plug and BF fitting | 10 |  |
| 14 | Cylinder connector LOR DN150 ANSI600 weldable with LOR plug and BF fitting | 9 |  |
| 15 | Cylinder connector LOR DN200 ANSI600 weldable with LOR plug and BF fitting | 6 |  |
| 16 | Closure fitting DN80xDN100 d 89 mm with LOR flange, plug with clamp fitting, BF fitting | 3 | Part 3 - Closure fittings |
| 17 | Closure fitting DN100xDN100 d 108 mm with LOR flange, plug with clamp fitting, BF fitting | 2 |  |
| 18 | Closure fitting DN100xDN100 d 114 mm with LOR flange, plug with clamp fitting, BF fitting | 2 |  |
| 19 | Closure fitting DN125xDN150 d 133 mm with LOR flange, plug with clamp fitting, BF fitting | 2 |  |
| 20 | Closure fitting DN150xDN150 d 159 mm with LOR flange, plug with clamp fitting, BF fitting | 2 |  |
| 21 | Closure fitting DN150xDN150 d 168 mm with LOR flange, plug with clamp fitting, BF fitting | 1 |  |
| 22 | Closure fitting DN200xDN200 d 219 mm with LOR flange, plug with clamp fitting, BF fitting | 13 |  |
| 23 | Closure fitting DN250xDN250 d 273 mm with LOR flange, plug with clamp fitting, BF fitting | 1 |  |
| 24 | Closure fitting DN300xDN300 d 324 mm with LOR flange, plug with clamp fitting, BF fitting | 4 |  |
| 25 | Closure fitting DN350xDN350 d 356 mm with LOR flange, plug with clamp fitting, BF fitting | 1 |  |
| 26 | Closure fitting DN400xDN400 d 406 mm with LOR flange, plug with clamp fitting, BF fitting | 1 |  |
| 27 | Closure fitting DN430xDN450 d 426 mm with LOR flange, plug with clamp fitting, BF fitting | 1 |  |
| 28 | Bypass connector DN150xDN100 d 159 mm with LOR flange, plug with clamp-on connector, BF fitting | 2 | Part 4 - Bypass connectors |
| 29 | Bypass connector DN200xDN100 d 219 mm with LOR flange, plug with clamp-on connector, BF fitting | 1 |  |
| 30 | Bypass connector DN250xDN150 d 273 mm with LOR flange, plug with clamp-on connector, BF fitting | 2 |  |
| 31 | Bypass connector DN300xDN150 d 324 mm with LOR flange, plug with clamp-on connector, BF fitting | 2 |  |
| 32 | Bypass connector DN400xDN200 d 406 mm with LOR flange, plug with clamp-on connector, BF fitting | 1 |  |

* The quantities quoted are prelimanary, for pricing and comparability purposes. The quantities submitted are subject to change without altering the unit price or other conditions of performance.

  - BYPASS FLANGE - a set of components for use in an existing pipeline as a bypass element or cylinder connection. The set consists of: flange set - blind, neck with LOR-type plug, bolt and nut set, two steel multi-layer gaskets with graphite insert, spare O-ring gasket.

  - AIR VENT CONNECTION - a connection with a special internal plug used for venting the gas inside sealed appliances from an isolated section of the pipeline, or used as a cylinder connection.

  - CYLINDER CONNECTOR - a welded steel connector on an existing gas pipeline for the introduction of insulating cylinders into the interior of the pipeline. The set includes: flange set - blind, neck with LOR-type plug, welded part (or other technical solution approved by the Technical Service), bolt and nut set with two steel multi-layer gaskets with graphite insert.

  - LOR CYLINDER CONNECTOR - a welded steel connector on an existing gas pipeline for the introduction of insulating cylinders into the interior of the gas pipeline. The set includes: flange set - blind, neck with LOR-type plug, welded part, as well as a set of bolts and nuts, two steel multi-layer gaskets with graphite insert, spare O-ring gasket.

  - CLOSING FITTINGS - set of components with a LOR plug, a set of bolts and nuts and a blind. For installation in operational gas pipelines. The design of the connections shall ensure the safe closure of the elements and the isolation and sealing of the active pipeline section. The set (per fitting) shall include: a bolt and nut kit, a blind flange, a spare LOR O-ring, two steel multi-layer gaskets with graphite insert and outlet plates.

  - BYPASS FITTING (BF) - Component set with LOR plug, bolt and nut kit and blind. For installation in operational gas pipelines. The design of the fittings must ensure that these elements close securely.

2.     Main pipeline design parameters:

2.1. Maximum operating pressure		5,4 MPa.

2.2. Ambient temperature              from -35 °C to +50 °C.

2.3. Gas fuel temperatures                     from -10 °C to +50 °C.

2.4. Design code			B31.8

2.5. Design factor                          0,72

2.6. Design pressure			54 barai

2.7. Flange class			600 PN64

2.8. Flange surface			RF

3.   Delivery and documentation

3.1. The delivery of the items must be accompanied by documents on paper or on any electronic medium. Documents can be sent by post or email. The items are delivered with documents to the following address: Gudelių str. 49, Vilnius, Lithuania.

3.2. Technical safety verification document

3.3. Declaration of conformity.

3.4. Certificates for materials.

3.5. Results of non-destructive testing;

3.6. Separate documents (technical drawings) shall be provided for each fitting after manufacture. Common documentation must be provided for connectors and nozzles, grouped into a range;

3.7. Documentation shall be provided for individual components to be ordered, such as bolts, nuts, washers and gaskets, confirming their conformity with this Description of the Object of the Order and the applicable standards;

3.8. Each material ordered must be clearly marked (e.g. engraved) by the manufacturer with a nameplate or an identifiable number or mark to link the range to a specific quality document.

3.9. Technical manufacturing documents;

3.10. Declarations;

5.     Anti-corrosion protection.

5.1. The required paint layer is either an epoxy primer or a zinc phosphate-based two-component acrylic polyurethane paint. Coating thickness 80-120 micrometres.

5.2. The Supplier should certify compliance with these requirements by means of an appropriate declaration.

5.3. Parts not coated with paint and not susceptible to corrosion by other materials should be protected by temporary protective measures. Visible corrosion or traces of corrosion on materials is not permitted.

6.     Acceptance

6.1. The object of the Agreement shall be accepted at a specific location within a time limit agreed by the Parties, together with the relevant accompanying documents.

6.2. The Supplier shall notify the Customer's representative electronically at least 2 days in advance of the readiness for delivery and of the chosen delivery location. Failure to notify the Customer shall relieve the Customer of its obligation to accept the object of the Agreement.

6.3. The Customer - reserves the right to assess the conformity of the procurement object with the requirements set out in the Proposal, the Technical Specification, the Description of the object of the Agreement and the Agreement, at the location specified by the Supplier or at the Supplier's place of manufacture, prior to the delivery of the object of the Agreement to the delivery location. Following the initial assessment, a preliminary inspection protocol will be drawn up. Preliminary protocol shall not constitute a basis for invoicing for the object of the Agreement and shall not constitute a basis for any other claims against the Customer. Signature of the Preliminary inspection protocol does not constitute acceptance of the object of the Agreement.

6.4. The Supplier shall properly pack and protect the object of the Agreement during transport to ensure that it is delivered to the Customer in good condition.

The Supplier shall be liable for any damage caused during packing, transport and unloading.

6.5. In the event of defects which impair the value or usefulness of the object of the Agreement for the purpose specified in the Agreement, the Supplier undertakes to compensate the Customer for the reasonable loss.

6.6. If any defects (including qualitative or quantitative defects) are found upon acceptance of the object of the Agreement, the Customer shall have the right to refuse to accept the object of the Agreement or to accept the defective part of the object of the Agreement delivered.

Defects which are grounds for refusal to accept part or all of the object of the Agreement shall be recorded in the acceptance protocol.

6.7. Acceptance of the object of the Agreement will be confirmed by an Acceptance act of the object of the Agreement signed by authorised representatives of both Parties.

6.8. After the Customer has signed the acceptance act with comments, the Supplier shall be entitled to reply to the Customer's comments within 5 working days.

6.9. In the event of observations, the Customer may also set a new one-off deadline for the Supplier to deliver the object of the Agreement without defects. If the Supplier meets the specified additional delivery date, the contractual penalties for the relevant part of the object of the Agreement shall not apply. In the event of non-compliance with this additional delivery date, the contractual penalties will be calculated for the delay from the original due date. The acceptance procedure shall be repeated (without the possibility of an additional time limit) for the object of the Agreement which has been rejected by the Customer with observations in accordance with the provisions of this clause.

6.10. Acceptance of the object of the Agreement without comments shall not relieve the Supplier of liability for latent defects, which shall be notified to the Supplier by the Customer without delay.

6.11. If, at the time of acceptance of the object of the Agreement at the place of delivery, there is a dispute as to any defects in the object of the Agreement, the Parties shall appoint an acceptance committee. The acceptance committee shall consist of 4 (four) persons, two appointed by the Customer and two by the Supplier. If the work of the acceptance committee does not lead to a unanimous conclusion, the Parties shall appoint an independent expert. The costs of the expert's investigation shall be borne by the Party to whose disadvantage the conclusions of the said investigation are drawn. The results of the investigation, including its costs, will be included in a report prepared by the expert and signed by the Parties. If the acceptance committee or the independent expert confirms that the object of the Agreement is defective, the time spent by the acceptance committee or the independent expert shall be qualified by the Parties as a delay in the performance of the Agreement attributable to the Contractor.

6.12. Having adopted a position according to clause 6.9, the Parties shall proceed in accordance with the provisions of this clause with respect to the acceptance of the object of the Agreement.

6.13. At the Customer's request, all or part of the object of the Agreement may be received at the Supplier's premises or at the place of storage or manufacture of the object of the Agreement.

6.14. Upon signature by the Customer of the Protocol of Acceptance of the Object of the Agreement, the ownership of the object of the Agreement, to which the Customer has not objected, shall pass to the Customer. As from that date, the Customer shall assume the obligations and risk of accidental loss or damage to the object of the Agreement.

6.15. The Customer shall not be liable for the risk of loss, damage or destruction of the object of the Agreement left by the Supplier and not collected by the Customer in the event of a refusal to take delivery or in the cases referred to in clause 4 or 14.

6.16. If the Supplier delivers the object of the Agreement by courier, the Customer shall acknowledge receipt of delivery in the presence of the courier. Within 5 working days of receipt of delivery, the Customer shall inspect the object of the Agreement in terms of quantity and quality, confirming conformity or notifying defects in the transfer-acceptance protocol. The Supplier's liability to the Customer shall not be limited by the terms of the Supplier's cooperation with the entities involved in the organisation and delivery of the object of the Agreement.

6.17. The Supplier shall deliver the ordered items to the address specified by the Customer at its own effort, expense and risk. Materials are accepted on working days between 8:00 a.m. and 2:00 p.m. (Monday to Friday, except statutory public holidays).

18) The fittings shall be mounted on wooden pallets (europallets) capable of withstanding the loads during transport and long-term storage and shall be protected against accidental damage and weathering.

19) Gaskets shall be packed in a single package for each diameter. It shall be stored and transported in such a way as to protect it from damage, atmospheric conditions and chemical and mechanical contamination.

20) Nuts and bolts shall be packed in a single package for each diameter and shall be stored and transported in such a way as to be protected against damage, atmospheric conditions, chemical and mechanical contamination.

8.    EU origin

The Customer shall require that the proportion of products originating in the Member States of the European Union or countries with which the European Union has concluded agreements on equal treatment between Member States or countries to which the provisions of Directive 2014/25/EU apply in accordance with the Council Decision, in respect of parts No. 1, No. 2, No. 3 and No. 4, shall be greater than 50 %.

9.     Delivery location:

Gudelių str. 49, Vilnius, Lithuania.

10.   Implementation deadlines:

7 months after signing the agreement

  - The price(s) of the proposal shall be indicated in the following tables:

Table 1

| No. | Name | Quantity | Unit price, EUR excl. VAT | Amount, Eur excl. VAT |
| --- | --- | --- | --- | --- |
| 1. | Drilling equipment for drilling holes in existing high-pressure gas pipelines (5,4 MPa) DN80-DN400 and plugging the existing pipeline | 1 pcs. |  |  |
| 1.1. | Optional installation for the drilling equipment for drilling holes in DN80-DN400 diameter in high pressure (5,4 MPa) gas pipelines and for plugging the pipeline. |  |  |  |
| 1.1.1 | The drive unit - a diesel hydraulic unit with an electric starting system. Structure with transport frame, lifting eyelets. The unit must be suitable for transport by forklift truck and jib crane. Includes hydraulic hoses to connect the drilling equipment and the drive unit, with 1", 3/4" and 3/8" hose diameters and a minimum length of 15 metres, with quick couplings at the ends compatible with the Contracting Party's range of equipment. | 1 set |  |  |
| 1.1.1.1 | Cutter holders for diameters from 3" to 16" | 1 pcs. |  |  |
| 1.1.1.2 | LOR-type plug holder for diameters from DN100 (4") to DN400 (16") | 1 pcs. |  |  |
| 1.1.1.3 | Linestop cutter 4"-100 mm, | 2 pcs. |  |  |
| 1.1.1.4 | Linestop cutter 6"-150 mm | 2 pcs. |  |  |
| 1.1.1.5 | Linestop cutter 8"-198 mm | 2 pcs. |  |  |
| 1.1.1.6 | Linestop cutter 10"-248 mm | 2 pcs. |  |  |
| 1.1.1.7 | Linestop cutter 12"-298 mm | 2 pcs. |  |  |
| 1.1.1.8 | Linestop cutter 14"-332 mm | 2 pcs. |  |  |
| 1.1.1.9 | Linestop cutter 16" -383 mm for pipe OD-406 mm | 2 pcs. |  |  |
| 1.1.1.10 | Linestop cutter 16" for pipe OD-426 mm | 2 pcs. |  |  |
| 1.1.1.11 | Incising cutter 4"-87 mm | 2 pcs. |  |  |
| 1.1.1.12 | Incising cutter 6"-139 mm | 2 pcs. |  |  |
| 1.1.1.13 | Incising cutter 8" -186mm | 2 pcs. |  |  |
| 1.1.1.14 | Incising cutter 10" -241mm | 2 pcs. |  |  |
| 1.1.1.15 | Incising cutter 12" -292mm | 2 pcs. |  |  |
| 1.1.1.16 | Incising cutter 14" -324mm | 2 pcs. |  |  |
| 1.1.1.17 | Incising cutter 16"-373 mm for pipe OD-406 mm | 2 pcs. |  |  |
| 1.1.1.18 | Incising cutter 16" for pipe OD-426 mm | 2 pcs. |  |  |
| 1.1.1.19 | "Hottap" adapter 4" with 3/8" and 1" NPT connectors | 2 pcs. |  |  |
| 1.1.1.20 | "Hottap" adapter 6" with 3/8" and 1" NPT connectors | 2 pcs. |  |  |
| 1.1.1.21 | "Hottap" adapter 8" with 3/8" and 2" NPT connectors | 2 pcs. |  |  |
| 1.1.1.22 | "Hottap" adapter 10" with 3/8" and 2" NPT connectors | 2 pcs. |  |  |
| 1.1.1.23 | "Hottap" adapter 12" - 323,9 mm, with 3/8" and 2" NPT connectors | 2 pcs. |  |  |
| 1.1.1.24 | "Hottap" adapter 12" - 325 mm, with 3/8" and 2" NPT connectors | 2 pcs. |  |  |
| 1.1.1.25 | "Hottap" adapter 14" with 3/8" and 2" NPT connectors | 2 pcs. |  |  |
| 1.1.1.26 | "Hottap" adapter 16" - 406 mm, with 3/8" and 2" NPT connectors | 2 pcs. |  |  |
| 1.1.1.27 | "Hottap" adapter 16" - 426 mm, with 3/8" and 2" NPT connectors | 2 pcs. |  |  |
| 1.1.1.28 | 4" guiding drill | 4 pcs. |  |  |
| 1.1.1.29 | 6" guiding drill | 4 pcs. |  |  |
| 1.1.1.30 | 8" guiding drill | 4 pcs. |  |  |
| 1.1.1.31 | 10" guiding drill | 4 pcs. |  |  |
| 1.1.1.32 | 14" guiding drill | 4 pcs. |  |  |
| 1.1.1.33 | 16" guiding drill - 406 mm | 4 pcs. |  |  |
| 1.1.1.34 | Small machine pneumatic drive motor | 1 pcs. |  |  |
| 2. | Drilling equipment for drilling holes in existing high-pressure gas pipelines (5.4 MPa) DN50-DN150 | 1 pcs. |  |  |
| 2.1. | Additional equipment for drilling machine for drilling holes in diameters DN50-DN150 and plugging holes in high pressure gas pipelines (5.4 MPa) DN50-DN150 |  |  |  |
| 2.1.1 | Plug holder for diameters DN50 to DN100 | 1 pcs. |  |  |
| 2.1.2 | Cutter holder for diameters DN50-DN150 "size-on-size" | 2 sets |  |  |
| 2.1.3 | Cutter holder for DN50-DN150 diameters "non size-on-size" | 2 sets |  |  |
| 2.1.4 | Cutter for hole d-98,4 mm (3-7/8") | 2 pcs. |  |  |
| 2.1.5 | Drill bit d-36,5 mm (1-7/16") | 2 pcs. |  |  |
| 2.1.6 | Thread adapter DN50 with 2" NPT tapered male thread | 2 pcs. |  |  |
| 2.1.7 | Threaded adapter DN80 with 2" and 3" NPT tapered male threads | 2 pcs. |  |  |
| 2.1.8 | Flange adapter DN80 - (3") ANSI class 600 | 1 pcs. |  |  |
| 2.1.9 | Flange adapter DN100 - (4") ANSI class 600 | 1 pcs. |  |  |
| 3. | GENERAL REQUIREMENTS FOR EQUIPMENT 1 AND 2 (SET) |  |  |  |
| 3.1. | Hydraulic cylinders for shutting off pipelines of diameter DN100-DN400 at a pressure of 5,4 MPa |  |  |  |
| 3.1.1 | Hydraulic linestop drive for 4"-12", used with plugging housings and heads, for lowering the plug into the pipeline and shutting off the flow; after the work is done, removing the plug and thus fully restoring the flow at a pressure of 5,4 MPa. | 2 sets |  |  |
| 3.1.2 | Hydraulic linestop drive for 14"-20", used with plugging housings and heads, for lowering the plug into the pipeline and shutting off the flow; after the work is done, removing the plug and thus fully restoring the flow at a pressure of 5,4 MPa. | 2 sets |  |  |
| 4. | Closure housings, heads and seals |  |  |  |
| 4.1. | Closure housing DN100-4" ANSI 600 class with 3/8" and 1" NPT female threaded connectors | 2 pcs. |  |  |
| 4.2. | Closure housing DN150-6" ANSI 600 class with 3/8" and 1" NPT female threaded connectors | 2 pcs. |  |  |
| 4.3. | Closure housing DN200-8" ANSI 600 class with 3/8" and 2" NPT female threaded connectors | 2 pcs. |  |  |
| 4.4. | Closure housing DN300-12" ANSI 600 class with 3/8" and 2" NPT female threaded connectors | 2 pcs. |  |  |
| 4.5. | Closure housing DN350-14" ANSI 600 class, OD-406mm, with 3/8" and 2" NPT female threaded connectors | 2 pcs. |  |  |
| 4.6. | Closure housing DN350-16" ANSI 600 class, OD-406mm, with 3/8" and 2" NPT female threaded connectors | 2 pcs. |  |  |
| 4.7. | Closure housing DN350-16" ANSI 600 class, OD-426mm, with 3/8" and 2" NPT female threaded connectors | 2 pcs. |  |  |
| 4.8. | Closing head DN100 ANSI 600 class with nozzle kit for pipes ID DN100 - 4" | 2 pcs. |  |  |
| 4.9. | Closing head DN150 ANSI 600 class with nozzle kit for pipes ID DN150 - 6" | 2 pcs. |  |  |
| 4.10 | Closing head DN200 ANSI 600 class with nozzle kit for pipes ID DN200 - 8" | 2 pcs. |  |  |
| 4.11 | Closing head DN300 ANSI 600 class with nozzle kit for pipes ID DN300 - 12" | 2 pcs. |  |  |
| 4.12 | Closing head DN350 ANSI 600 class with nozzle kit for pipes ID DN350 - 14" | 2 pcs. |  |  |
| 4.13 | Closing head DN400 OD-406 mm ANSI class 600, with nozzle kit, for pipes ID DN350-16" | 2 pcs. |  |  |
| 4.14 | Closing head DN400 OD-426 mm ANSI class 600, with nozzle kit, for pipes ID DN350-16" | 2 pcs. |  |  |
| 4.15 | 4" sealing elements | 4 pcs. |  |  |
| 4.16 | 6" sealing elements | 4 pcs. |  |  |
| 4.17 | 8" sealing elements | 4 pcs. |  |  |
| 4.18 | 10" sealing elements | 4 pcs. |  |  |
| 4.20 | 12" sealing elements | 4 pcs. |  |  |
| 4.21 | 14" sealing elements | 4 pcs. |  |  |
| 4.22 | 16" sealing elements | 4 pcs. |  |  |
| 4.23 | 17" Sealing elements, for pipe OD 426 mm | 4 pcs. |  |  |
| 5. | Sandwich valves from DN100-4" to DN400-16" ANSI 600 class |  |  |  |
| 5.1. | Sandwich valve DN100 - 4" ANSI 600 class | 2 pcs. |  |  |
| 5.2. | Sandwich valve DN150 - 6" ANSI 600 class | 2 pcs. |  |  |
| 5.3. | Sandwich valve DN200 - 8" ANSI 600 class | 2 pcs. |  |  |
| 5.4. | Sandwich valve DN300 - 12" ANSI 600 class | 2 pcs. |  |  |
| 5.5. | Sandwich valve DN350 - 14" ANSI 600 class | 2 pcs. |  |  |
| 5.6. | Sandwich valve DN400 - 16" ANSI Class 600 for pipes OD-406 mm | 2 pcs. |  |  |
| 5.7 | Sandwich valve DN400 - 16" ANSI 600 class, for pipes OD-426 mm | 2 pcs. |  |  |
| 6. | Theoretical and practical training in the operation and maintenance of the equipment, followed by training by the supplier in the periodic maintenance of the equipment. The training must be provided in Lithuanian. | 6 people |  |  |

| Price of the tender in EUR excluding VAT |  |
| --- | --- |
| VAT** |  |
| Price of the Tender in EUR including VAT |  |

Table 2

| No. | Description | Quantity | Unit price, EUR excl. VAT | Amount, EUR excl. VAT |
| --- | --- | --- | --- | --- |
| 1 | Bypass flange DN100 ANSI600 with LOR plug and BF fitting | 11 |  |  |
| 2 | Bypass flange DN150 ANSI600 with LOR plug and BF fitting | 12 |  |  |
| 3 | Bypass flange DN200 ANSI600 with LOR plug and BF fitting | 8 |  |  |
| 4 | Bypass flange DN250 ANSI600 with LOR plug and BF fitting | 6 |  |  |
| 5 | Bypass flange DN300 ANSI600 with LOR plug and BF fitting | 4 |  |  |
| 6 | Bypass flange DN400 ANSI600 with LOR plug and BF fitting | 4 |  |  |
| 7 | Threaded ventilation connector DN50 | 40 |  |  |
| 8 | Threaded ventilation connector DN80 | 30 |  |  |
| 9 | Cylinder connector DN80 ANSI600 without plug with BF fitting | 5 |  |  |
| 10 | Cylinder connector DN100 ANSI600 without plug with BF fitting | 4 |  |  |
| 11 | Cylinder connector DN150 ANSI600 without plug with BF fitting | 3 |  |  |
| 12 | Cylinder connector DN200 ANSI600 without plug with BF fitting | 4 |  |  |
| 13 | Cylinder connector LOR DN100 ANSI600 weldable with LOR plug and BF fitting | 10 |  |  |
| 14 | Cylinder connector LOR DN150 ANSI600 weldable with LOR plug and BF fitting | 9 |  |  |
| 15 | Cylinder connector LOR DN200 ANSI600 weldable with LOR plug and BF fitting | 6 |  |  |
| 16 | Closure fitting DN80xDN100 d 89 mm with LOR flange, plug with clamp connector, BF fitting | 3 |  |  |
| 17 | Closure fitting DN100xDN100 d 108 mm with LOR flange, plug with clamp connector, BF fitting | 2 |  |  |
| 18 | Closure fitting DN100xDN100 d 114 mm with LOR flange, plug with clamp connector, BF fitting | 2 |  |  |
| 19 | Closure fitting DN125xDN150 d 133 mm with LOR flange, plug with clamp connector, BF fitting | 2 |  |  |
| 20 | Closure fitting DN150xDN150 d 159 mm with LOR flange, plug with clamp connector, BF fitting | 2 |  |  |
| 21 | Closure fitting DN150xDN150 d 168 mm with LOR flange, plug with clamp connector, BF fitting | 1 |  |  |
| 22 | Closure fitting DN200xDN200 d 219 mm with LOR flange, plug with clamp connector, BF fitting | 13 |  |  |
| 23 | Closure fitting DN250xDN250 d 273 mm with LOR flange, plug with clamp connector, BF fitting | 1 |  |  |
| 24 | Closure fitting DN300xDN300 d 324 mm with LOR flange, plug with clamp connector, BF fitting | 4 |  |  |
| 25 | Closure fitting DN350xDN350 d 356 mm with LOR flange, plug with clamp connector, BF fitting | 1 |  |  |
| 26 | Closure fitting DN400xDN400 d 406 mm with LOR flange, plug with clamp connector, BF fitting | 1 |  |  |
| 27 | Closure fitting DN430xDN450 d 426 mm with LOR flange, plug with clamp connector, BF fitting | 1 |  |  |
| 28 | Bypass connector DN150xDN100 d 159 mm with LOR flange, plug with clamp connector, BF fitting | 2 |  |  |
| 29 | Bypass connector DN200xDN100 d 219 mm with LOR flange, plug with clamp connector, BF fitting | 1 |  |  |
| 30 | Bypass connector DN250xDN150 d 273 mm with LOR flange, plug with clamp connector, BF fitting | 2 |  |  |
| 31 | Bypass connector DN300xDN150 d 324 mm with LOR flange, plug with clamp connector, BF fitting | 2 |  |  |
| 32 | Bypass connector DN400xDN200 d 406 mm with LOR flange, plug with clamp connector, BF fitting | 1 |  |  |
| Price of the proposal in EUR excluding VAT |  |  |  |  |
| VAT** |  |  |  |  |
| Price of the proposal in EUR including VAT |  |  |  |  |

The price of the proposal in EUR including VAT must include all costs, all taxes and charges payable in accordance with the applicable laws of the Republic of Lithuania.

** If the Supplier is not a VAT payer or if the services are exempt from VAT in accordance with the Law on Value Added Tax of the Republic of Lithuania, the “VAT” shall be set to 0 and the “Proposal price in EUR incl. VAT” shall be set to the same amount as the “Proposal price in EUR exl. VAT”. If the Supplier is not subject to VAT or if the services are exempt from VAT or are subject to reduced VAT, the Supplier must provide a justification for the exemption from VAT or for the reduced VAT rate.

The price of the proposal in EUR including VAT must include all costs, all taxes and charges payable in accordance with the applicable laws of the Republic of Lithuania.

** If the Supplier is not a VAT payer or if the services are exempt from VAT in accordance with the Law on Value Added Tax of the Republic of Lithuania, the “VAT” shall be set to 0 and the “Tender price in EUR incl. VAT” shall be set to the same amount as the “Tender price in EUR exl. VAT”. If the Supplier is not subject to VAT or if the services are exempt from VAT or are subject to reduced VAT, the Supplier must provide a justification for the exemption from VAT or for the reduced VAT rate.