TECHNICAL SPECIFICATION

- DEFINITIONS AND ABBREVIATIONS

1.1. Client – UAB Kauno kogeneracinė jėgainė

1.2. Service Provider – an economic entity, a natural person, a private legal entity, a public legal entity, other

organisations and their subdivisions or a group of such persons with whom the Client enters into a Contract.

1.3. Contract – the Contract concluded between the Client and the Service Provider in relation to the Subject

Matter of the Contract.

1.4. Services – cleaning of boiler surfaces with controlled gas mixture explosions and mechanically.

1.5.     Order – a written order submitted to the Service Provider on the basis of the Contract by text message, email and/or through the information system specified by the Client, specifying the quantities, delivery addresses, and the deadline of the Services.

1.6. Mobilisation – arrival and departure at the address specified in Part 4 of the Technical Specification, including travel, accommodation, and other related costs.

- SUBJECT MATTER OF THE CONTRACT

  - Cleaning with controlled explosions and mechanical cleaning of boiler flue systems.

- PIRKIMO OBJEKTO APIMTYS

  - The quantities of the Services are given in Table 1 below:

Lentelė Nr. 1

| No. | Name of the Services | Unit of Measurement | Preliminary Quantity for the Duration of the Contract |
| --- | --- | --- | --- |
|  | Mobilization (mobilization includes: transportation of personnel and equipment, accommodation, site preparation, assembly and dismantling of equipment, ensuring work area safety, coordination meeting, acceptance of work with the client). | Vnt. | 18 |
|  | Cleaning of boiler steam overheat surfaces with controlled gas mixture explosions. During boiler operation. (Online Cleaning). | Vnt. | 18 |
|  | Cleaning of boiler steam overheat surfaces using pneumatic tools or abrasive cleaning. After switching off the boiler. (Offline Cleaning). | Vnt. | 5 |

- PLACE OF PROVISION OF THE SERVICES

  - The Services shall be provided: Kaunas District, Biruliškės village, Jėgainės Str. 6 LT-54469.

- REQUIREMENTS FOR THE SUBJECT MATTER OF THE CONTRACT

Description of the Subject Matter of the Contract

5.1. Cleaning of boiler steam overheat surfaces with controlled gas mixture explosions while the boiler is operating. A water-cooled probe with a special bag is introduced into the boiler steam overheats through hatches near the heating surface to be cleaned. The bag is inflated with the gas mixture and the flammable mixture ignites. Shock waves or vibrations of the pipes and walls remove ash deposits. The composition of the gas mixture and the explosion strength are determined according to the amount of contamination. The boiler must remain in operation during the explosion.

5.2. Cleaning the boiler’s steam overheat surfaces using pneumatic tools or abrasive cleaning after the boiler is switched off. If necessary, the Service Provider will be required to carry out mechanical cleaning of the boiler steam overheats after the surfaces have been cleaned with explosions. The boiler shall be shut down and the overheat surfaces shall be cleaned with pneumatic tools and/or glass, corundum, quartz or other abrasive materials. The method of cleaning shall be selected according to the amount of contamination of the boiler overheats. The abrasive materials required for mechanical cleaning shall be supplied by the Client. 5.3. Any cleaning work on the boiler must not damage parts of the boiler. To ensure the safety of equipment and personnel.

5.4. The unit of measurement for the Services shall be treated (Table 1, Lines 2-3) as the time required to provide the Service, not exceeding 8 hours.

- PROCEDURES AND DEADLINES FOR THE PROVISION OF SERVICES

6.1. The Services must be provided no later than within 10 (ten) days from the day of submission of the Order to the Service Provider.

6.2. The Service Provider shall provide the Services at the address(es) specified in Part 4 of the Technical

Specification during the Client’s working hours (7:30 a.m. to 4:30 p.m. Mon-Thu, 7:30 a.m. to 3:15 p.m. Fri).

6.3. A period of 3 (three) days shall be set, within which the Client must accept the Services (i.e. sign the

statement of handover and acceptance of the result of the Services).

- KOKYBĖ IR TRŪKUMŲ PAŠALINIMAS

7.1. Deficiencies in the Services and/or in the result of the Services shall be deemed to be a superheated steam temperature of < 450C when the boiler is operating at nominal load (107 T/h).

7.2. The Client shall have the right to apply to the Service Provider for the rectification of any deficiencies in the Services and/or the result of the Services no later than within 7 (seven) days of the date of signing the statement of handover and acceptance of the provided Services/identification of the deficiencies.

7.3. The following deadline shall be set to address any deficiencies in the results of the Services identified

by the Client: 5 (five) days.

- TERMS OF PAYMENT

8.1. The Client shall pay the Service Provider for quality Services that were provided actually within 30 (thirty) days of the date of signing of the statement of handover and acceptance of the result of the Services and receipt of the Invoice.

- DOCUMENTS ACCOMPANYING THE SERVICES PROVIDED

9.1. The statement of handover and acceptance of the result of the Services.

Preliminary quantity of the Service is specified. Throughout the duraation of the Contract, the Client shall have the right to adjust the quantity Services purchased, up tp the maximum price of the Contract specified in the Contract. The client shall not be obliged to purchase all or any part of the Services.