TECHNICAL SPECIFICATION

- TERMS AND ABBREVIATIONS

  - Contracting Entity – AB Amber Grid.

  - Supplier, Contractor – an economic operator (a natural person, private legal entity, public legal entity, other organization and its divisions, or a group of such persons, including temporary associations of economic operators) that offers to perform works, supply goods, or provide services related to the Procurement Object.

  - Contract – an agreement concluded between the Contracting Entity and the Supplier awarded the procurement contract for the Procurement Object.

  - DAS (Distributed Acoustic Sensing) – a technology based on the use of optical fibre as a continuous sensor for detecting and monitoring acoustic and vibration events.

  - Tele-signalling System – an advanced pipeline monitoring system operating on the principle of Distributed Acoustic Sensing (DAS). The system consists of hardware and software components, including potential modifications to the fibre-optic cable infrastructure. The system utilizes a fibre-optic cable installed alongside the transmission gas pipeline as a sensor array, enabling the real-time detection and analysis of acoustic and vibration signals over long distances.

  - FAT (Factory Acceptance Test) – factory acceptance testing performed prior to delivery of the system to the Facility.

  - SAT (Site Acceptance Test) – acceptance testing performed at the installation site following system deployment.

  - TPI (Third-Party Interference) – unauthorized third-party activity or impact on infrastructure (e.g., excavation works, movement of heavy machinery) posing a risk to the safety and integrity of transmission gas pipelines and detectable using DAS technology.

  - Facility – Santaka Gas Metering and Pressure Regulating Station (Santaka GMPRS), located at Išlandžių k. 16, Liudvinavas Eldership, Marijampolė District Municipality, Lithuania.

  - Optical Fibre Loop Point – an optical distribution panel located within the territory of the Republic of Poland (approximate coordinates in the WGS-84 coordinate system: 54.227131, 23.351329).

  - Facility Readiness – the condition under which the Contracting Entity ensures: (i) physical access to the Facility; (ii) backup electrical power supply at the Facility; (iii) preparation of remote workstation equipment; (iv) an operational data communication link between the central and remote workstations; (v) access to optical fibre connections at the Facility; and (vi) the required remote access connectivity.

  - Coverage Area – a strip of land extending along the fibre-optic cable, covering an area 10 metres on each side of the cable, including the subsurface beneath this strip. The beginning of the Coverage Area is defined as the intersection of the fibre-optic cable and the perimeter fence of the Santaka GMPRS (approximate length of the Coverage Area – 20 km), while the end of the Coverage Area is defined as the intersection of the fibre-optic cable and the outer perimeter fence of the Optical Fibre Loop Point.

- PROCUREMENT OBJECT

  - Procurement Object – services for the design, taking into account the characteristics of the Facility, rental, transportation, installation, configuration, technical support and dismantling of the Tele-signalling System and related equipment.

  - Main objectives of the Procurement Object:

    - To provide the Contracting Entity with a fully operational DAS-based solution for temporary use, enabling a comprehensive assessment of the benefits offered by DAS technology for transmission gas pipeline monitoring, with particular emphasis on reducing the risk of pipeline rupture and improving the reliability of gas supply.

    - To measure and validate the capability of DAS technology to accurately detect, classify and localize Third-Party Interference (TPI) events, as well as to assess the technology’s sensitivity and false alarm rates under real operating conditions, thereby determining the overall reliability of DAS technology and the potential workload imposed on the Contracting Entity’s personnel.

    - To collect factual data on the capital expenditures (CAPEX), operational expenditures (OPEX), and the economic benefits associated with the Tele-signalling System.

- SCOPE OF PROCUREMENT

  - List and Sequence of Services to Be Provided by the Supplier:

| No. | Service | Service Description |
| --- | --- | --- |
| 1. | Preparatory Works |  |
| 1.1. | Project Implementation Schedule Development | Preparation of a project implementation schedule, e.g. in Gantt chart format, covering the sequence of all service delivery stages specified in the Technical Specification. |
| 2. | Design |  |
| 2.1. | Assessment of the Contracting Entity’s Technological Assets and Electronic Communications Infrastructure | Assessment of the existing electronic communications infrastructure, including ODF/optical connections, power supply, rack/equipment installation space, data transmission capabilities, cable routes, etc. If the Supplier determines that an on-site inspection is required, the timing of the inspection shall be coordinated with the Contracting Entity. |
| 2.2. | Hardware Design and Identification of the Need for Modifications to Existing Data Transmission Equipment, if Required | Preparation of the hardware solution design, including component composition, interconnections, required accessories, installation materials, etc., taking into account the Facility parameters and the requirements of the Technical Specification. Identification of the need for adaptation and, if necessary, modification of the existing data transmission infrastructure. |
| 2.3. | Completion of FAT | Preparation of the FAT report documenting that the Tele-signalling System hardware has successfully passed factory acceptance testing prior to delivery to the Contracting Entity. |
| 3. | Equipment Installation Services | Commencing on the date the Contracting Entity issues the Facility Readiness Notice to the Supplier. |
| 3.1. | Preparation of the Existing Technological Network for Proper Operation of the Tele-signalling System | - Installation of temporary modifications at the Optical Fibre Loop Point (installation works shall be carried out by the Contracting Entity) and at the Facility. - OTDR measurements of the fibre-optic cable fibres and determination of the actual attenuation values. - Installation of temporary data transmission lines within the Contracting Entity’s premises. - Preparation of the data transmission lines for the Tele-signalling System. Note: The Contracting Entity shall establish a dedicated network segment for the Tele-signalling System for data transmission between the central and remote workstations and shall perform the required network configuration |
| 3.2. | Equipment Installation at the Facility | Installation shall be performed in consultation with the Contracting Entity and in accordance with applicable legal requirements and the Contracting Entity’s internal procedures. Connection of equipment to the Facility’s 230 V power supply shall be carried out by the Contracting Entity’s specialists. |
| 3.3. | Preparation of Installation Completion Documentation | - Preparation of an installation completion documentation package confirming that the equipment has been installed and is ready for the configuration and SAT phases. - The documentation shall be prepared in a manner that ensures full traceability of all temporary solutions/modifications implemented during installation, including the solutions at the Optical Fibre Loop Point installed by the Contracting Entity in consultation with the Supplier. |
| 4. | Configuration |  |
| 4.1. | Optical Channel Adjustment | - Adjustment of DAS interrogator parameters to the Contracting Entity’s electronic communications infrastructure, including the fibre-optic cable located within the Coverage Area. - Software configuration of blind spots where monitoring is not possible (e.g. server rooms, fibre-optic splice closures, etc.). |
| 4.2. | Geographic Referencing | - Correlation of the physical fibre-optic cable length with the actual geographical coordinates and kilometre markers of the pipeline. - Upload of the digital pipeline route map to the operator workstation and accurate visualization of the route in the user interface. |
| 4.3. | Zoning and Virtual Barrier Creation | - Division of the entire monitored section into logical zones based on the surrounding environment (e.g. "Road Crossing", "River Crossing", etc.) and assignment of different sensitivity parameters to each zone according to its characteristics. |
| 4.4. | Configuration of Detection Algorithms and Classifiers | - Activation and configuration of algorithms designed to recognize specific acoustic signatures (e.g. "Manual Excavation", "Mechanical Excavation", "Gas Leak", etc.) in accordance with the characteristics of the Coverage Area. - Software filtering of continuous non-hazardous noise sources (e.g. constant road traffic). |
| 4.5. | User Interface Customization | - Configuration of alarm visualization and assignment of user access rights. |
| 4.6. | Iterative Configuration and Optimization / Fine-Tuning | - Continuous monitoring of background acoustic conditions over a defined period in order to collect data on actual environmental conditions. - Review and analysis of false alarms generated by the system, if any. - Calibration of sensitivity thresholds and detection algorithms based on the collected data in order to eliminate recurring false alarms without reducing true detection sensitivity. |
| 5. | Testing and Commissioning |  |
| 5.1. | Preparation for SAT and Commissioning | Preparation of SAT methodology and test scenarios in accordance with the requirements of the Technical Specification. |
| 5.2. | SAT Execution | SAT shall be carried out with the participation of representatives of both the Supplier and the Contracting Entity. During SAT, it shall be verified that the Tele-signalling System is properly installed and configured, transmits data, generates alarms, displays events in the user interface, and complies with the requirements of the Technical Specification and the acceptance criteria defined in the SAT methodology. |
| 5.3. | Completion of SAT | - Preparation of the SAT Report documenting that the Tele-signalling System has successfully passed the acceptance tests and complies with the requirements of the Technical Specification. - The SAT Report shall specify the indicative maximum false alarm rate for the relevant monitored section over a defined period under normal meteorological conditions. |
| 5.4. | Personnel Training | Practical training for the Contracting Entity’s personnel, up to five specialists. |
| 5.5. | Documentation Preparation and Handover for Operation | - Preparation of the Tele-signalling System User Manual in Lithuanian or English. - Execution of the Tele-signalling System Acceptance and Handover Act. |
| 6. | Equipment Decommissioning Upon Expiry of the Tele-signalling System Rental Period |  |
| 6.1. | Data Archiving and Secure Deletion | - Transfer of all data collected during the operational period, including alarm logs, system status reports and selected acoustic recordings, to storage media designated by the Contracting Entity. - Secure deletion of sensitive information from the Supplier’s information systems in accordance with the Contracting Entity’s security policy. |
| 6.2. | Physical Removal of Equipment and Restoration of the Technological Network | If the Contracting Entity’s technological network or any equipment located within the Coverage Area has been modified, the following activities shall be performed: - Removal of temporary modifications and restoration of the technological assets and equipment to their original condition. - OTDR measurements of the fibre-optic cable fibres, documenting and confirming that the fibre-optic cable remained undamaged following equipment removal and that its performance parameters comply with the specified requirements. |
| 6.3. | Completion of Equipment Removal Activities | Preparation of an inspection report confirming that no damage was caused to the property of either the Contracting Entity or the Supplier during equipment removal. |
| 6.4. | Equipment Collection and Transportation | Collection of equipment from the Contracting Entity’s premises, during the Contracting Entity’s working hours, in consultation with the Contracting Entity. |
| 7. | Other Services |  |
| 7.1. | Technical Support Services | Technical support in English or Lithuanian during the Contracting Entity’s working hours through e-mail, telephone, Microsoft Teams or an equivalent secure communication platform, and not less than 10 hours of remote technical consultations. |
| 7.2. | Support Services | Provision of all software licences required for operation of the Tele-signalling System throughout the rental period. |

- GENERAL REQUIREMENTS FOR THE PROCUREMENT OBJECT

  - At the Supplier’s request, a site visit to the Facility may be arranged in relation to the Procurement Object. Any Supplier interested in participating in the procurement procedure and submitting a proposal may inspect the Facility by contacting the Contracting Entity and providing the positions, names and surnames of the persons intending to participate in the visit, as well as a proposed date and time for the visit (the Contracting Entity reserves the right to reschedule the visit). In response to such request, the Contracting Entity shall specify the date and time of the visit for each Supplier.

  - For the price specified in its proposal, the Supplier shall perform all works specified in the Technical Specification, as well as any ancillary works and activities that are technologically necessary by their nature, directly arising from the requirements of the Technical Specification, the technical characteristics of the Facility, and which a diligent supplier operating in the relevant field could reasonably have identified and assessed at the time of submission of the proposal. This provision shall not apply to works that change the scope of the Procurement Object, the technical requirements, or require additional solutions not specified by the Contracting Entity.

  - For the price specified in its proposal, the Supplier shall undertake to perform all activities related to equipment installation at the Facility, programming, tuning, configuration and testing, and shall deliver a fully operational Tele-signalling System for operation by the Contracting Entity, by completing the SAT Report and executing the Tele-signalling System Acceptance and Handover Act no later than 15 calendar days from the date on which the Contracting Entity issues the Facility Readiness Notice to the Supplier. Iterative configuration and optimization shall be carried out for no less than 2 calendar days following the initial commissioning of the system. SAT shall be performed after completion of the optimization period unless the Parties agree otherwise in writing.

  - The indicative Facility Readiness date, provided for planning purposes only, is 1 March 2027. This date does not constitute a contractual commitment of the Contracting Entity towards the Supplier, and any change to this date shall not be deemed a material amendment to the Contract or procurement conditions, provided that the scope, price and technical requirements of the Procurement Object remain unchanged.

  - Within 20 business days following the expiry of the rental period, the Supplier, in consultation with the Contracting Entity, shall dismantle and remove the Tele-signalling System hardware and all related components from the installation locations.

  - Throughout the entire rental and operational period of the Tele-signalling System, the Supplier shall ensure that the Tele-signalling System operates in accordance with the requirements of the Technical Specification.

  - If, during the rental and operational period, the Tele-signalling System or any part thereof fails to operate, operates with faults, or does not comply with the requirements of the Technical Specification, the Supplier shall commence fault correction without delay and no later than the day following receipt of the Contracting Entity’s notification. Any fault or malfunction that renders the Tele-signalling System unusable for its intended purpose shall be rectified within 24 hours from receipt of the Contracting Entity’s notification, unless the Parties agree otherwise in writing, taking into account the nature of the fault. If rectification within the specified period is not possible, the Supplier shall, at its own expense, replace the defective equipment or part thereof, or provide an equivalent technical solution ensuring compliance of the Tele-signalling System with the requirements of the Technical Specification. Faults and malfunctions arising from equipment, software, licences, configuration, tuning, maintenance activities or any other actions provided by the Supplier shall be rectified at the Supplier’s expense. If it is determined that a fault or malfunction is caused by the Contracting Entity’s infrastructure, actions of the Contracting Entity’s personnel, or third parties for whom the Supplier is not responsible, the Supplier shall provide consultation and technical assistance in identifying and resolving the issue, but shall only be liable to the extent that the issue arose due to incorrect or incomplete instructions provided by the Supplier. Any period during which the Tele-signalling System is unavailable or cannot be used for its intended purpose due to reasons attributable to the Supplier shall not be counted towards the rental and operational period. In such cases, the rental and operational period shall be extended by an equivalent duration at no additional cost to the Contracting Entity. Upon rectification of the fault or malfunction, the Supplier shall provide the Contracting Entity with a report specifying the cause of the fault, the corrective actions taken, the resolution time, and, where applicable, measures proposed to prevent recurrence.

  - The Tele-signalling System, including all related telecommunications and electronic communications components, shall be designed in such a manner that maintenance requirements are minimized.

  - The Tele-signalling System shall consist of standardized hardware and software components, except where manufacturer-specific components are necessary due to the nature of the proposed technology. In such cases, the Supplier shall identify the non-standard components in its proposal and justify their necessity.

  - The Tele-signalling System shall be installed in a manner that minimizes the risk of damage to the Contracting Entity’s electronic communications infrastructure.

  - The Supplier shall be responsible for the installation and proper operation of any additional network infrastructure installed within the territory of the Republic of Lithuania. Within the territory of the Republic of Poland, physical installation works shall be carried out or arranged by the Contracting Entity in accordance with the technical instructions provided in writing by the Supplier in advance. The Supplier shall be responsible for the accuracy of the instructions provided and for technical consultation, but shall not be liable for improperly performed installation works carried out by the Contracting Entity or persons engaged by it, unless such improper performance resulted from incorrect or incomplete instructions supplied by the Supplier.

  - All software, software installation packages and other files required for provision of the Services shall be submitted to the Contracting Entity for verification not later than 20 business days prior to commencement of any activities involving their use.

- TELE-SIGNALLING SYSTEM HARDWARE AND SOFTWARE REQUIREMENTS

  - The performance of the Tele-signalling System shall meet or exceed the specified requirements. If equipment meeting a specific level cannot be provided, equipment of a higher specification level shall be proposed.

  - The values of all parameters specified in the Technical Specification shall not be artificially increased or enhanced beyond the manufacturer's standard specifications.

  - The following mandatory requirements for the Tele-signalling System shall be fully complied with in the Supplier's proposal:

| No. | Requirement | Parameter / Value |
| --- | --- | --- |
| GENERAL REQUIREMENTS |  |  |
| 1 | System Architecture and Remote Monitoring | The Supplier shall configure the system so that monitoring, system control and visualization are available at two workstations: • a central workstation, with the equipment provided by the Supplier; • a remote workstation, with the equipment provided by the Contracting Entity. The Supplier shall install and configure software on the remote workstation to ensure comprehensive real-time data visualization and system control. |
| 2 | Optical Channel Multi-Pass Looping Using Parallel Fibres | The Supplier shall provide an optical route interconnection solution enabling the DAS interrogator’s optical signal to be transmitted multiple times forwards and backwards through the same fibre-optic cable by sequentially switching the signal through several parallel fibres within the cable. The solution shall enable testing of equivalent optical path configurations of approximately 20 km, 40 km, 60 km and 80 km. At the Optical Fibre Loop Point and the Facility, it shall be possible to establish all Configurations A–D by means of patching, without additional fibre splicing during testing. Fibre connection works at the Optical Fibre Loop Point shall be performed by the Contracting Entity. The Supplier shall provide the required connectors, optical adapters and terminators. The Supplier shall verify the connections from the Facility, for example by means of OTDR and/or optical power-loss measurements, and confirm that the system is correctly connected in accordance with the selected configuration, complies with the Technical Specification and operates without interruption. Configurations: A: approximately 20 km – a single-fibre terminator shall be installed at the Optical Fibre Loop Point, if required for the selected equipment. B: approximately 40 km – a two-fibre loop shall be installed at the Optical Fibre Loop Point; the terminator, if applicable, shall be installed at the Facility. C: approximately 60 km – a two-fibre loop and a terminator, if applicable, shall be installed at the Optical Fibre Loop Point; a two-fibre loop shall be installed at the Facility. D: approximately 80 km – two two-fibre loops shall be installed at the Optical Fibre Loop Point; a two-fibre loop and a terminator, if applicable, shall be installed at the Facility. SC/APC ODF panels are used at the Facility and the Optical Fibre Loop Point. Eight spare fibres are available in the fibre-optic cable between the Facility and the Optical Fibre Loop Point. The solution shall enable all four looping configurations to be tested during the project. |
| 3 | Compatibility with Existing Electronic Communications Infrastructure | The system shall be compatible with the Contracting Entity’s electronic communications infrastructure, including the fibre-optic cable located within the Coverage Area. |
| 4 | Cable Integrity Monitoring | The system shall be capable of monitoring fibre-optic cable parameters in real time and automatically detecting a fibre break or significant signal degradation, including identification of the fault location. |
| 5 | Operating Conditions | System components shall operate under the conditions present at the Facility and within the Coverage Area and shall have an ingress protection rating and ambient operating temperature range suitable for those conditions. |
| 6 | Uninterruptible Power Supply | A separate uninterruptible power supply is not required. The hardware shall be connected to the Contracting Entity’s backed-up power supply at the Facility, comprising a three-phase UPS and a diesel generator. |
| 7 | Automatic Recovery | The system shall start automatically (auto-boot) and resume monitoring following the loss and subsequent restoration of electrical power. |
| 8 | Internal Diagnostics | The system shall continuously monitor its internal components, including the DAS interrogator, storage media, temperature and other relevant parameters, and shall automatically generate fault notifications or technical alarms indicating the system status. |
| 9 | Remote Access | The system shall support out-of-band (OOB) remote access functionality. |
| 10 | Remote Manual Reboot | The system shall allow users to restart the system manually via remote access in the event of a software freeze, error or other malfunction. |
| 11 | Time Synchronization | An integrated GPS module shall be provided for precise time synchronization. |
| 12 | DAS Interrogator Operating Temperature | The DAS interrogator unit shall operate at an ambient temperature from 0°C to 40°C. |
| 13 | CE Marking | System components shall bear the CE marking. |
| TECHNICAL REQUIREMENTS |  |  |
| 14 | Signal Measurement Principle | The system shall operate on the principle of Coherent Optical Time-Domain Reflectometry (COTDR). |
| 15 | Monitoring Range | Not less than 60 km per channel without optical amplification. |
| 16 | Number of Optical Channels | Not less than one channel. |
| 17 | Spatial Resolution | The minimum configurable spatial resolution value shall not exceed 5 metres. |
| 18 | Frequency Band | The system shall detect signals within a frequency range no narrower than 0.5 kHz to 2.5 kHz. |
| MONITORING REQUIREMENTS |  |  |
| 19 | Signal Classification | The system shall support classification algorithms, including machine-learning algorithms, to distinguish target threats, such as excavation works and movement of machinery, from environmental interference, such as rain, wind and trains. |
| 20 | Multi-Point Detection | The system shall be capable of detecting and tracking several independent events occurring simultaneously at different pipeline locations, for example manual digging at kilometre 5 and a gas leak at kilometre 10. |
| 21 | Real-Time Event Recognition | The system shall process incoming acoustic data in real time and automatically generate an alarm when a signal exceeds a defined noise threshold or exhibits specific characteristics. |
| 22 | Event Location Determination | The system shall automatically calculate and assign a geographical location, including coordinates and a kilometre marker, to each detected event. |
| 23 | Event Location Accuracy | The maximum location error shall not exceed 10 metres throughout the entire monitored section. |
| 24 | TPI Event Detection and Classification | The system shall recognize, distinguish from environmental noise and classify the following specific TPI events within the Coverage Area in real time: manual excavation, mechanical excavation, vehicle movement and pedestrian movement. |
| 25 | TPI Event Detection Time | The period from the start of an event until generation of an alarm shall not exceed: • manual digging – 10 minutes; • mechanical digging – 3 minutes; • vehicle movement – 1 minute. |
| 26 | PIG Tracking Module | A specialized module operating independently of the TPI module and automatically detecting, identifying and tracking the movement of a PIG (Pipeline Inspection Gauge) in real time based on its acoustic signature, including friction and vibration. |
| 27 | Gas Leak Detection Module | A specialized module operating independently of the TPI module and using advanced algorithms to identify gas releases. |
| GRAPHICAL USER INTERFACE REQUIREMENTS |  |  |
| 28 | Spatial Resolution Adjustment | The user shall be able to select and change the spatial resolution while the system is operating. |
| 29 | Spectral Event Review — Historical Data | The system shall provide a function for reviewing historical spectral representations of acoustic data, such as spectrograms or waterfall plots, for a selected event period for post-event analysis. |
| 30 | Interference Suppression | The system shall provide a function for disabling detection at specific points, such as near a compressor or road intersection, in order to reduce false alarms. |
| 31 | Virtual Zoning | The system shall allow the entire monitored length of optical cable to be divided into zones and shall allow individual sensitivity and alarm settings to be assigned to each zone. |
| 32 | GIS Visualization | The transmission gas pipeline route shall be displayed on a geographical map with a satellite-image background and linked to the physical cable length and the actual kilometre markers of the pipeline route. The Contracting Entity shall provide a DWG-format drawing of the cable route. |
| 33 | Alarm Management | Alarm indications shall remain active on the screen until manually acknowledged by the operator. The system shall allow alarms to be acknowledged individually or in groups. The data-viewing interface shall be interactive and shall include zoom and scrolling functions enabling the event location and time to be identified accurately. |
| 34 | Spectral Visualization of Acoustic Data | The system shall generate a real-time representation of acoustic data in the user interface in the form of a spectral diagram (waterfall plot). The diagram shall correlate the event location, expressed as distance or kilometre marker, and time with the intensity of the acoustic signal. |
| 35 | Data Export for Analysis | It shall be possible to export the alarm log for a selected period in a text-based format, such as CSV, TXT or equivalent. |
| 36 | User Access Rights Management | The system’s authorization mechanism shall be based on a role-based access-control model. Different access levels, such as Administrator, Engineer and Operator, shall be provided, restricting the ability of users without the appropriate authorization to change system settings. |
| 37 | Password Complexity | The system shall enable full configuration of the password policy, including, but not limited to, minimum password length, uppercase and lowercase letters, numbers, special characters, password validity period, number of failed login attempts and other relevant parameters. The exact parameters shall be agreed during installation. |
| 38 | Password Encryption | Passwords shall not be stored in plain text within the system. |
| 39 | Automatic User Logout | The system shall allow configuration of a user-session inactivity period, after which an inactive user shall be logged out automatically. |
| 40 | Client Workstation | The system shall support remote access through an encrypted HTTPS web interface and/or a dedicated client application. |
| SECURITY REQUIREMENTS |  |  |
| 41 | Data Retention | Alarm data shall be retained for no less than four weeks. |
| 42 | Data Integrity | Collected event data shall not be editable or deletable at the Operator access level, thereby protecting the data against tampering. |
| 43 | GDPR Compliance | The software and the Supplier shall comply with the personal-data protection principles and requirements established by Regulation (EU) 2016/679 (GDPR). |
| 44 | Prohibition of External Decryption | Sensitive and/or confidential information within the software shall not be capable of being decrypted externally. |
| 45 | Prevention of Plain-Text Password Storage | The software shall not store passwords in plain text. |
| 46 | Use of Licensed Hardware and Software | The Supplier shall ensure that only authorized and properly licensed hardware and software are used in the development and provision of the system. |
| 47 | Encrypted Software Repository | The software shall be stored in an encrypted repository. |
| 48 | Cryptographic Key Management and Minimum Key Length | Cryptographic keys shall be used in the software and their security shall be ensured. The key length shall be no less than 256 bits. |
| 49 | Prohibition of Hidden and Malicious Functions | The software shall not contain hidden functions that weaken security, including malware, viruses, worms, time bombs, unauthorized access mechanisms or functions, Trojans, backdoors or Easter eggs. A responsible subcontractor or manufacturer may be engaged for implementation. |
| 50 | Protection Against Malicious Attacks | Measures shall be implemented to protect against malware and malicious attacks, including, where applicable, Intrusion Prevention Systems and Intrusion Detection Systems (IPS/IDS), firewalls and antivirus software. |
| ACCESS AUDIT AND MANAGEMENT |  |  |
| 51 | Audit Log Collection and Retention | The software shall collect and retain, throughout the project implementation period, audit information relating to data operations, including actions, users, dates and timestamps. |
| 52 | Audit Record Review Functionality | Authorized users shall be able to review information relating to specific audit records easily, both on screen and in reports. |
| 53 | Audit Record Immutability | Audit records shall be protected against unauthorized or accidental modification. Users shall not be permitted to modify records while reviewing them. |
| 54 | Prevention of Editing Administrator Activity Logs | Software administrators shall not be permitted to delete or edit log records relating to administrator activities. |
| 55 | General Prohibition on Editing Audit Records | Software audit records shall not be editable or otherwise modifiable. |
| 56 | Email Configuration and Restrictions | The system shall provide email configuration functionality and the ability to restrict any automatic or manual forwarding of emails to mailboxes that do not belong to the Contracting Entity. |
| 57 | Data Ownership and Transfer | The Contracting Entity shall own the data stored in the software. Upon termination of the Services, the data shall be transferred to the Contracting Entity in accordance with the agreed scope and deadlines. |
| 58 | User Identification and Session Management | The software shall uniquely identify users and ensure that sessions are terminated after the configured period of inactivity. |
| 59 | Infrastructure and Information Protection | The software infrastructure and the Contracting Entity’s information contained therein shall be protected against unauthorized access, copying or any other form of unauthorized reproduction or recovery. |
| 60 | Forwarding of Log Records to SIEM | It shall be possible to forward log records in Syslog format to a centralized Security Information and Event Management (SIEM) system for log collection and processing. |

- DESCRIPTION OF THE CURRENT SITUATION

  - Technical Characteristics of the Facility:

| No. | Technical Characteristic | Value / Condition |
| --- | --- | --- |
| 1 | Room ventilation and air conditioning | Yes |
| 2 | Available space for installation of the DAS equipment rack | Width: 1,000 mm Length: 1,200 mm Height: 2,000 mm |
| 3 | Distance between the proposed equipment rack location and the optical distribution frame (ODF) | Approximately 2 metres |
| 4 | Optical distribution frame (ODF) connector configuration | 24 × SC/APC duplex, single-mode |
| 5 | Available electrical power and voltage | 700 W at 230 VAC; 400 VAC is also available |

  - Technical Characteristics of the Optical Fibre Loop Point:

| No. | Technical Characteristic | Value / Condition |
| --- | --- | --- |
| 1 | Optical Distribution Frame (ODF) Connector Type | SC/APC |

  - Measurement Data for the Optical Fibre Dedicated to the Tele-signalling System (from Santaka GMPRS to the Optical Fibre Loop Point):

| No. | Technical Characteristic | Value / Condition |
| --- | --- | --- |
| 1 | Measurement Date | 29 October 2021 |
| 2 | Measured Line Length | 20.08 km |
| 3 | Maximum Attenuation of the Dedicated Optical Channels (Fibres) at 1310 nm | 6.84 dB |
| 4 | Maximum Attenuation of the Dedicated Optical Channels (Fibres) at 1550 nm | 4.62 dB |

- GENERAL SECURITY REQUIREMENTS

  - Cybersecurity Incident Management:

    - If the Supplier identifies or becomes aware of a cybersecurity incident within the infrastructure under its control that may affect the Contracting Entity’s data or information assets, the Supplier shall immediately, but in any event no later than within 24 (twenty-four) hours of identifying or becoming aware of such incident, provide the Contracting Entity with an early warning notification.

    - Within 72 hours of becoming aware of the incident, the Supplier shall submit a detailed notification specifying:

      - the nature and extent of the incident;

      - assessment of its impact;

      - the initial measures implemented.

    - At the request of the Contracting Entity, the Supplier shall submit interim reports and a final report.

    - The Contracting Entity shall specify to the Supplier the required content of the interim and final reports and the deadlines for their submission. The Supplier shall prepare and submit such reports in accordance with the Contracting Entity’s instructions and the incident-reporting obligations established under the Law on Cybersecurity of the Republic of Lithuania and by the National Cyber Security Centre (NCSC).

    - Notification Channels: Notifications shall be submitted to the Contracting Entity’s employees responsible for the performance of the Contract or to the Contracting Entity’s information security representatives. The information provided shall be authentic and, if requested, encrypted.

  - The following requirements shall apply to the work equipment used by the Supplier’s employees:

    - The hardware used shall be supported by its manufacturer and shall have all security patches released by the manufacturer installed, including firmware updates.

    - A valid and operational antivirus solution compliant with international security standards, such as ESET, Microsoft Defender for Endpoint or an equivalent solution, shall be installed. The antivirus software shall not originate from countries whose manufacturers or products may, under applicable legislation, pose a threat to national security, as defined in Article 50(9) of the Law of the Republic of Lithuania on Procurement Performed by Contracting Entities Operating in the Water, Energy, Transport or Postal Services Sectors. Accordingly, the antivirus software used shall not conflict with the national security requirements applicable to the Contracting Entity. At the request of the Contracting Entity, the Supplier shall provide information on the manufacturer and country of origin of the antivirus software used.

  - Data Processing and Storage:

    - Data Minimization: The Contracting Entity undertakes not to use, copy or retain more of the Supplier’s information than is necessary to achieve the purposes of the Contract.

    - Data Encryption:

      - Encryption at Rest: All information belonging to the Contracting Entity and temporarily stored on the Supplier’s devices shall be encrypted, for example by using BitLocker or FileVault.

      - Encryption in Transit: All data transmitted over networks shall be encrypted using secure protocols, such as TLS 1.3, SFTP or VPN.

    - Prohibition on the Use of Personal Resources: Processing the Contracting Entity’s information using personal email accounts, unapproved cloud services or personal storage media is strictly prohibited.

    - Data Localization: The Supplier shall ensure that all data belonging to the Contracting Entity are stored and processed only within the territory of Member States of the European Union (EU) or the European Economic Area (EEA), or in countries for which the European Commission has adopted an adequacy decision regarding the level of data protection. Any transfer of data outside these jurisdictions shall be permitted only with the Contracting Entity’s prior written consent.

  - Actions Following Expiry or Termination of the Contract:

    - Secure Data Transfer and Destruction:

      - All information belonging to the Contracting Entity shall be transferred securely to the Contracting Entity in the agreed format.

      - At the request of the Contracting Entity, the Contracting Entity’s information shall be destroyed (deleted) without delay, but no later than within 30 (thirty) calendar days of receipt of the request, taking into account technical, organizational and economic feasibility. Information that remains in backup copies due to technical limitations shall be deleted automatically and irreversibly as part of the normal backup retention cycle, but no later than within 90 (ninety) calendar days. At the request of the Contracting Entity, the Supplier shall provide written confirmation of destruction in the form of a data destruction certificate.

      - At the request of the Contracting Entity, the Supplier shall provide written confirmation, in the form of a data destruction certificate, that all information belonging to the Contracting Entity has been destroyed.

  - The Contracting Entity reserves the right, subject to giving the Supplier at least 60 (sixty) calendar days’ prior notice, to audit the security measures implemented by the Supplier in order to verify compliance with the requirements set out in this Technical Specification. The Contracting Entity may conduct the audit using its own resources or engage independent third-party representatives (auditors). The Supplier shall cooperate with the Contracting Entity and/or its appointed representatives during the audit.

- PROCEDURE AND DEADLINES FOR THE PERFORMANCE OF CONTRACTUAL OBLIGATIONS

  - The initial rental and use period of the Tele-signalling System shall be 3 (three) months. This period shall commence on the date of signing the Tele-signalling System Acceptance and Handover Act, provided that the SAT Report has been signed and the system has been handed over to the Contracting Entity for use.

  - The Contracting Entity shall have the right to extend unilaterally the rental and use period of the Tele-signalling System for no more than 3 (three) additional months, in three separate extensions of 1 (one) month each. The Contracting Entity shall notify the Supplier of each extension in writing no later than 10 (ten) calendar days in advance. Upon expiry of the rental and use period of the Tele-signalling System, including any extension thereof, the Supplier shall perform the data transfer, data destruction, equipment dismantling, technological network restoration and equipment removal activities specified in the Technical Specification.

  - Before carrying out any work at the Contracting Entity’s Facility, the Supplier shall, in accordance with the procedure established in the Procurement Contract, submit all required documents and obtain AB Amber Grid’s written authorization to perform work at an operating natural gas transmission system facility or installation, or within its protection zone, in accordance with the Procedure for Obtaining Authorization to Perform Work: https://www.ambergrid.lt/saugumas/darbai-perdavimo-sistemos-objektuose/sutikimo-dirbti-suteikimo-tvarka/582 .

  - Work performed in a natural gas environment at the Contracting Entity’s facilities shall be carried out in accordance with the Contracting Entity’s publicly available Categories of Work Performed in a Gas Environment and the Safety Rules for Work Performed in a Flammable Gas Environment, approved by Order No. 1-191 of the Minister of Energy of the Republic of Lithuania of 28 September 2012, as amended by Order No. 1-155 of the Minister of Energy of the Republic of Lithuania of 25 June 2021: https://ambergrid.lt/saugumas/darbai-perdavimo-sistemos-objektuose/darbu-duju-aplinkoje-kategorijos/585 .