TECHNICAL SPECIFICATION

- DEFINITIONS AND ABBREVIATIONS

  - Order – a written document submitted to the Service Provider on the basis of the Contract by text message, e‑mail and/or via the information system specified by the Buyer, indicating the quantities of Services, delivery addresses and deadlines.

  - Related Services – services not specified in the technical specification but related to the purchased object. The total price of such Related Services may not exceed 10% of the initial Contract value.

- CHARACTERISTICS AND SCOPE OF THE PROCUREMENT OBJECT

  - Technical maintenance services of the waste boiler and supply of spare parts.

  - The quantities of services and goods are provided in Annex No. 1 to the Technical Specification.

Description of the Procurement Object

The technical maintenance services of the waste boiler operated at UAB Vilniaus kogeneracinė jėgainė include:

  - Inspection services for the boiler, the grate, and the feeders provided by the works supervisor:

    - The Work Supervisor shall perform a detailed inspection of the boiler, grate and feeders, including but not limited to inspection of feeder tables, guides, hydraulic cylinders, wear plates, grate bars, side and central wear plates, hydraulic cylinders, grate frame, grate sliding bearings, boiler pressure pipelines, headers, SNCR and AGAM openings, superheaters, evaporators and economiser.

    - During the inspection, the Service Provider must comply with all occupational safety and environmental protection requirements and perform inspections only from assembled and inspected scaffolding and platforms (to be installed by the Client).

    - After completing the inspection, the Work Supervisor shall submit an inspection report listing the identified deficiencies, required repairs and materials.

    - The Work Supervisor must be able to organise and supervise the elimination of defects in these systems.

  - Inspection services for the boiler, the grate, and the feeders provided by the  Work Executor:

    - The Work Executor shall perform a detailed inspection of the boiler, grate and feeders, including but not limited to inspection of feeder tables, guides, hydraulic cylinders, wear plates, grate bars, side and central wear plates, hydraulic cylinders, grate frame, grate sliding bearings, boiler pressure pipelines, headers, SNCR and AGAM openings, superheaters, evaporators and economiser.

    - During the inspection, the Service Provider must comply with all occupational safety and environmental protection requirements and perform inspections only from assembled and inspected scaffolding and platforms (to be installed by the Client).

    - After completing the inspection, the Work Executor shall provide insights to the Work Supervisor.

    - The Work Executor must be able to supervise fitters and welders to ensure defects in these systems are eliminated.

  - Inspection services for the boiler, the grate, and the feeders provided by the Welder

    - The Welder shall perform repair works of the boiler, grate and feeders, boiler pressure pipelines, headers, superheaters, evaporators and economiser.

    - During the works, the Service Provider must comply with all occupational safety and environmental protection requirements and perform works only from assembled and inspected scaffolding and platforms (to be installed by the Client).

  - Inspection services for boiler masonry repairs by the work supervisor

    - The Work Supervisor shall perform a detailed inspection of the masonry, including but not limited to visual inspection of the entire masonry, inspection of secondary air openings, feeder zone masonry, assessment of porosity and burnout level.

    - During the inspection, the Service Provider must comply with all occupational safety and environmental protection requirements and perform inspections only from assembled and inspected scaffolding and platforms.

    - After completing the inspection, the Work Supervisor shall submit an inspection report listing the identified deficiencies, required repairs and materials.

    - The Work Supervisor must be able to organise and supervise the elimination of defects in these systems.

  - Masonry Repair – Work Executor Services

    - The Work Executor shall perform a detailed inspection of the masonry, including but not limited to visual inspection of the entire masonry, inspection of secondary air openings, feeder zone masonry, assessment of porosity and burnout level.

    - During the inspection, the Service Provider must comply with all occupational safety and environmental protection requirements and perform inspections only from assembled and inspected scaffolding and platforms.

    - After completing the inspection, the Work Executor shall provide insights to the Work Supervisor.

    - The Work Executor must be able to supervise qualified masonry workers to ensure defects in these systems are eliminated.

  - Inspection services for boiler masonry repairs by a qualified worker

    - The Qualified Worker shall perform a detailed inspection of the masonry, including but not limited to visual inspection of the entire masonry, inspection of secondary air openings, feeder zone masonry, assessment of porosity and burnout level.

    - During the inspection, the Service Provider must comply with all occupational safety and environmental protection requirements and perform inspections only from assembled and inspected scaffolding and platforms.

    - After completing the inspection, the Qualified Worker shall provide insights to the Work Supervisor.

    - The Qualified Worker must be able to perform repair works to eliminate defects in these systems.

- PLACE, PROCEDURE AND DEADLINES FOR SERVICE PROVISION

  - Services are provided at: Paneriškių g. 25, Vilnius, UAB Vilniaus kogeneracinė jėgainė, during the Client’s working hours (Mon–Thu 7:30–16:30, Fri 7:30–15:15).

  - Services must be provided no later than within 10 working days from the date the Order is submitted to the Service Provider. To allow proper resource planning, the Client shall notify the Service Provider of the planned plant shutdown and preliminary works 3 months in advance, and clarify the information 1 month before the planned start of Services.

  - Materials/Goods must be delivered within the deadline specified in the Order, which may range from 2 weeks to 6 months.

  - Services will be provided only on the basis of separate Orders submitted by the Client during the term of the Contract.

  - The Order shall specify the scope of Services, title, start and end dates.

  - Service Provision Procedure:

    - Services shall be provided in accordance with applicable standards, norms and rules of the Republic of Lithuania and the European Union.

    - Materials, products and structures used for the Services must be certified in the Republic of Lithuania and the EU.

    - The Service Provider shall, within 5 working days from the Contract signing date and subsequently each January or upon changes, submit to the Client the completed Annex No. 1 “Work Request Form” of the Client’s Contractor Work Organisation Standard.

    - The Service Provider’s employees must wear special clothing with the Service Provider’s logo, and technical staff must wear a badge indicating their name and position.

    - The Service Provider’s employees must comply with the Client’s internal work rules.

    - The Service Provider shall ensure, at its own expense, all necessary safety, hygiene and fire‑fighting equipment.

    - The Service Provider shall provide the Services using its own resources, infrastructure and equipment, and at its own risk and expense procure all structures, devices, materials and other equipment required for the Services.

    - The Service Provider must provide all equipment necessary for inspections.

    - The Service Provider must provide all equipment necessary for working at height; such costs must be included in the Service price.

    - The Service Provider must ensure safe working conditions for its personnel and other contractors working in the same area.

    - The Service Provider shall repair its own tools, equipment and mechanisation means at its own expense.

    - The Client shall allow the Service Provider’s qualified personnel to use the Client’s lifting equipment operated remotely from the workstation.

    - The Service Provider must obtain, arrange and manage all permits, certificates, approvals and consents required for the Services, except those the Client must provide under the Contract.

    - The Service Provider must leave the work area tidy at the end of each working day and collect waste in the Client’s containers.

    - Scrap metal generated during repairs must be prepared for transport, transported by the Service Provider, and delivered on behalf of the Client to the scrap metal collection company designated by the Client.

    - The Service Provider must comply with the traffic rules established within the Client’s territory.

  - Requirements for Materials:

    - Materials supplied by the Service Provider must comply with applicable standards of the Republic of Lithuania and/or the EU. Materials certified outside the EU must be equivalent and meet Lithuanian and/or EU certification requirements.

    - Before the start of Services, together with the cost estimate, the Service Provider must submit certificates and quality documents confirming compliance with applicable standards.

    - The Order will specify which Materials must be supplied by the Service Provider and/or which will be supplied by the Client.

    - Upon receiving the Service Provider’s cost estimate, the Client shall approve it within 3 working days. After approval, a material handover act is signed, after which all responsibility for the materials transfers to the Service Provider.

  - Documents Submitted with the Services:

    - Service result handover‑acceptance act.

    - Boiler inspection and masonry condition assessment reports with defect lists and repair recommendations.

  - Documents listed in Clauses 3.8.1–3.8.2 shall be submitted in English.

- OTHER REQUIREMENTS

  - Service and/or Service result deficiencies are considered any non‑compliance with the Technical Specification or legal requirements governing service quality.

  - Services are accepted by signing the service handover‑acceptance act.

  - Service deficiencies shall be eliminated at the Service Provider’s expense throughout the Contract term unless otherwise specified.

  - The Service Provider shall provide a warranty of not less than 12 months for the Services and not less than 12 months for the Materials supplied (or the manufacturer’s warranty, if longer), starting from the date of signing the handover‑acceptance act.

  - The Client may request elimination of deficiencies during the entire warranty period.

  - A 5‑working‑day deadline is set for eliminating identified deficiencies.

  - If the Service Provider damages the Client’s equipment during the Services, causing emergency shutdowns, the Service Provider shall compensate direct losses determined by a joint commission.

  - No later than 3 working days before the start of Services, the Service Provider shall submit a written request for connecting its electrical equipment to the Client’s electrical network, indicating the responsible person.

- ANNEXES

Annex No. 1 – Preliminary scope of services and goods.