TECHNICAL SPECIFICATION (TS)

- DEFINITIONS AND ABBREVIATIONS

  - The Buyer is SC KN Energies.

  - The Supplier – the economic operator – shall mean a natural person, a private legal person, a public legal person, other organisations and divisions thereof or a group of such persons the Buyer enters into a Contract with.

  - The Contract shall mean the Contract concluded between the Supplier and the Buyer with regard to the Procurement object.

  - The Procurement object shall mean Services.

- PROCUREMENT OBJECT

- Services for measuring methane leaks, data analysis and report preparation (hereinafter referred to as the Procurement Object).

The Supplier shall offer the entire quantity/scope of the Procurement Object.

The Procurement Object is not divided into lots.

  - CURRENT SITUATION

Regulation (EU) 2024/1787 of the European Parliament and of the Council, which has entered into force, establishes mandatory requirements and legally binding obligations for energy sector companies regarding methane emissions measurement, monitoring, reporting, verification, and leak management. Under the newly established regulatory framework, the Buyer is required to ensure that methane emissions measurements at the LNG Terminal (hereinafter referred to as the Terminal), the floating storage and regasification unit “Independence” (hereinafter referred to as the Vessel), and the natural gas distribution station (hereinafter referred to as the Station) are carried out by an independent third party.

- REQUIREMENTS FOR THE PROCUREMENT OBJECT

| SERVICES FOR MEASURING METHANE LEAKS, DATA ANALYSIS AND REPORT PREPARATION |  |  |
| --- | --- | --- |
| - The Procurement Object is subject to green procurement requirements |  |  |
| The Buyer seeks to ensure that both its own activities and those of the Supplier have the least possible impact on the environment. Therefore: 3.1.1. During the public procurement procedure and the performance of the Agreement, communication between the Supplier and the Buyer shall be carried out exclusively by electronic means (through the CVP IS, telephone, e-mail, or other electronic communication channels); 3.1.2. All documentation related to the performance of the Agreement shall be submitted to and exchanged between the Buyer and the Supplier by electronic means (through the CVP IS, e-mail, or other electronic communication channels); 3.1.3. The Parties shall seek to execute the Agreement exclusively by electronic means (using electronic signatures); 3.1.4. The Supplier undertakes to reduce paper consumption, avoid unnecessary copying and printing of documents, and, where office supplies are used, ensure that they are made from recycled materials or are recyclable; 3.1.5. Where printing is necessary, the Supplier undertakes to use recycled paper that complies with the green procurement requirements approved by Order No. D1-508 of the Minister of Environment of the Republic of Lithuania of 28 June 2011 “On the Approval of the Description of the Procedure for Applying Environmental Protection Criteria in Green Public Procurement” (hereinafter referred to as the Description); 3.1.6. The Supplier undertakes to sort waste generated during the provision of the Services and to transfer recyclable or reusable waste to a duly authorized waste management operator, while disposing of non-recyclable and non-reusable waste at designated disposal facilities; 3.1.7. If goods, materials, or raw materials used by the Supplier during the performance of the Services must be supplied or delivered in secondary packaging, such packaging shall comply with the minimum environmental protection criteria applicable to packaging, unless this would conflict with hygiene requirements. Such packaging shall be considered recyclable packaging in accordance with the provisions of the Law of the Republic of Lithuania on Environmental Pollution Tax; 3.1.8. The Supplier undertakes to promote the use of low-emission vehicles by its personnel when travelling to the location where the Services are performed, provided that such vehicles comply with the green procurement requirements set out in the Description; 3.1.9. The Supplier undertakes to ensure that the most efficient routes are selected for its personnel travelling to the locations where the Services are performed; 3.1.10. The Supplier undertakes, where possible, to assign the specialist located closest to the anticipated place of performance of the Services; 3.1.11. The Supplier undertakes to ensure that its activities do not pollute the environment or pose a risk to human health, thereby complying with the environmental principle established in Clause 4.4.4 of the Description. |  |  |
| - Requirements relating to compliance with national security interests |  |  |
| 3.2.1. The Buyer shall reject the Supplier’s application or tender if at least one of the grounds set out in Article 58(4¹) of the Law on Procurement by Contracting Entities of the Republic of Lithuania is established. |  |  |
| - Requirements for the Services for the Inventory of the Vessel’s Gas Equipment and the Development of a Methane Leak Database |  |  |
| No. | Requirement | Compliance / Fulfilment of Requirement |
| 3.3.1. | Equipment inventory and creation of leakage database for the vessel. | Inventory the equipment and create database of system components in excel (.xlsx) format in accordance with the scope specified by the Buyer. |
| 3.4. Requirements for contact-based source-level methane leak measurement services at the Buyer’s physical facilities: Terminal, Vessel, Station |  |  |
| No. | Requirement | Compliance / Fulfilment of Requirement |
| 3.4.1. | The EN 15446 and EN 17682 methodologies, or their equivalents, shall be applied during the provision of services. | Services must be provided in accordance with and using the best available methodology (using EPA21 or LST EN 15446: 2008 or equivalent) and using the best measurement instruments available on the market; they must identify potential methane leak points, taking into account the recommendations set forth in the OGMP 2.0 guidelines and the requirements established in the Regulation. |
| 3.4.2. | Compliance of Measuring Instruments with the Requirements of the Regulation | The measuring instruments used for measurements must comply with the requirements of the Regulation (current version, as amended). |
| 3.4.3. | Measurement of methane concentration by contact using calibrated, high-sensitivity equipment | Measurements must be performed using the direct (contact) method (Type 2), using calibrated equipment with a minimum detection limit of no more than 1 ppm (e.g., FID, PID, TDLAS, or equivalent technology) that directly measures the concentration of methane in parts per million (ppm). |
| 3.4.4. | Labeling of components with methane leaks | During the measurement, the Service provider must physically label the components of the equipment where methane leaks are detected, regardless of their size. |
| 3.4.5. | Preliminary Coordination of Measurements and the Buyer's Participation | The Supplier’s employees may conduct measurements after coordinating with the purchaser’s designated representatives no later than 14 (fourteen) calendar days in advance. The Buyer’s designated representatives may participate in and accompany the Supplier during the measurements. |
| 3.5. Requirements for site-level methane leak measurement services at the Buyer’s physical facilities: the Terminal, the Vessel, the onshore section of the main gas pipeline, and the Station |  |  |
| 3.5.1. | During the provision of services, apply the methods specified in EN 15446 and EN 17682, or an equivalent standard. | The Supplier must measure the Buyer’s sites using the best available methodology for site-level measurements, utilizing its own and/or leased equipment, in accordance with the recommendations set forth in the OGMP 2.0 guidelines and the requirements established in the Regulation. |
| 3.5.2. | Compliance of Measuring Instruments with the Requirements of the Regulation | The measuring instruments used for measurements must comply with the requirements of the Regulation (current version, as amended). |
| 3.5.3. | Simultaneous methane measuring at the source and site levels | Site-level methane leak measurements must be conducted at the same time as contact-based source-level methane leak measurements in order to ensure the most accurate comparison of data possible. |
| 3.5.4. | Measurements under safe and optimal conditions | The Supplier must take weather conditions into account to ensure that measurements are taken only under safe and optimal conditions and in accordance with the manufacturers’ instructions for the measuring instruments. |
| 3.5.5. | Selecting Measurement Equipment Based on the Characteristics of the sites | The Supplier must assess the situation and select the most appropriate measuring equipment, taking into account the characteristics of the Buyer’s various sites. |
| 3.6. Requirements for Services related to the Analysis of Measurement Data and the Preparation of Reports |  |  |
| 3.6.1. | Preparation and Submission of Reports on Source-Level contact measurements | The Supplier must analyse the measurements and prepare a template for the measurement report. The report must specify the quantitative leakage values per unit of time (g/h) and the concentration measurement values (ppm) for the measured locations (points), as well as the date and time of the measurement, the measuring instrument, information about the operator who performed the measurements, location information, and the technical number of the pipeline or other equipment. The report template must be agreed upon in writing with the Buyer before physical measurements are carried out at the sites. The report must be submitted no later than 20 (twenty) calendar days after the contact source level measurements have been completed. |
| 3.6.2. | Basis for Unit Conversions and Description of Methodologies used in the Report | If the Supplier performed conversions of units of measurement while preparing the report, it must provide the conversion methodology, which must comply with applicable international standards, along with a detailed explanation, uncertainties, coefficients (if used in the conversion), and calculation errors, in order to avoid flow correlation errors. The Supplier must include in the report a description of each piece of measuring equipment and measurement methodology, as well as a justification for the choice of measurement technology. |
| 3.6.3. | Submission of a comparative report on the results of Source-Level and site-Level Measurement Data | The Supplier must compare the source-level contact measurements with the site-level measurement data. Submit a comparative report that complies with the requirements of the Regulation and the OGMP 2.0 recommendations. The report must be submitted no later than 20 (twenty) calendar days after the source-level and site-level measurements have been completed. |
| 3.6.4. | Comparison and Analysis of Measurement Data | When comparing contact source-level measurements with site-level measurement data, the Supplier must evaluate and describe the environmental conditions and the existing technological process, compare the measurement results, calculate discrepancies, errors, and uncertainties, and submit a site comparison report with conclusions and recommendations to ensure data consistency. The report must include a description of the equipment used for the measurements, the measurement methods employed, and the calculations performed. |
| 3.6.5. | Identification and Removal of Unaccounted methane quantities. | During the analysis, the Supplier must identify the amount of methane entering the site that is not attributable to the site and exclude it from the overall calculation of the facility’s methane emissions. |
| 3.7. Other Requirements |  |  |
| 3.7.1. | When carrying out measurements at the Buyer’s physical facilities, the Supplier shall comply with all occupational health and safety requirements established by the Buyer, taking into account the nature and risks of the Services provided. |  |
| 3.7.2. | The Supplier shall include in the price of methane leak measurement services all costs related to the performance of the Services, including the rental of measuring or other necessary equipment, specialist working time, and data processing. The specialist mobilization price shall include all mobilization expenses, including flights, transportation, accommodation, and travel-related costs. |  |
| 3.7.3. | All data collected about the facility during the performance of the Services by the Supplier shall be processed exclusively within the territory of the European Union. The collected information shall be treated as confidential and protected against unauthorized acquisition, interception, or use. Data protection shall be ensured in compliance with the European Union cybersecurity requirements set out in Directive (EU) 2022/2555. |  |
| 3.7.4. | The Buyer shall be the owner of all data collected during the provision of the Services. The Supplier undertakes not to disclose any data under its control, not to transfer such data to third parties, to ensure its adequate protection, and to safeguard all archived information processed and stored throughout the term of the Agreement from unauthorized access by third parties. Upon expiration or termination of the Agreement, the Supplier shall remove from its systems all archived data and all copies thereof, shall not transfer such data to any third parties, and, upon the Buyer's written request, shall irreversibly destroy all data provided by the Buyer and collected by the Supplier, including data relating to facilities, employees, equipment, measurement data, and reports, no later than within 15 (fifteen) business days. The Supplier shall confirm the destruction of such data by means of a duly signed official written statement. |  |
| 3.7.5. | The Supplier shall immediately notify the Buyer of any actual or potential data misappropriation, data leakage, or cybersecurity incidents affecting the infrastructure and shall take all necessary measures to contain the incident and eliminate associated risks. |  |

3.8. DESCRIPTION OF THE PROCUREMENT OBJECT

The Buyer seeks to procure services for the measurement of methane leaks, data analysis, and report preparation:

- -    Services for conducting an inventory of the vessel’s gas equipment and creating a database of methane leak data;

- -    Services for measuring methane leaks at the source level at the Buyer’s physical facilities: the Terminal, the Vessel, and the Station;

- -    Services for measuring methane leaks at the site level at the Buyer’s physical facilities: the Terminal, the Vessel, the onshore section of the main gas pipeline, and the Station;

- -    Services for analysing the measurement data and preparing reports.

- SCOPE OF THE PROCUREMENT OBJECT

  - Pricing Model:

☒ Fixed Price

4.2.  The exact quantity is specified. The Contract Price shall be equal to the Supplier’s tender price excluding VAT. The Buyer undertakes to purchase the entire specified quantity of the Services.

| No. | Description | Unit | Quantity |
| --- | --- | --- | --- |
| 1. | - Inventory of Ship Equipment and Creation of a Leakage Database | lot | 1 |
| 2. | - Source-Level Methane Leak Detection Services for the Vessel | lot | 1 |
| 3. | - Contact-based source-level methane leak measurement services at Pier No. 157 | lot | 1 |
| 4. | - Contact-based source-level methane leak detection services at Valve Stations No. 1 and No. 2 | lot | 1 |
| 5. | - Contact-based source-level methane leak measurement services at the LNG reloading station | lot | 1 |
| 6. | - Contact-based source-level methane leak measurement services at the gas distribution station | lot | 1 |
| 7. | - Site-Level Methane Leak Detection Services for the vessel | lot | 1 |
| 8. | - Site-Level Methane Leak Measurement Services at Pier No. 157 | lot | 1 |
| 9. | - Site-Level Methane Leak Detection Services for an Onshore Gas Pipeline with Valve Stations | lot | 1 |
| 10. | - Site-Level Methane Leak Measurement Services at the Gas Metering Station | lot | 1 |
| 11. | - Site-Level Methane Leak Detection Services at the LNG reloading station | lot | 1 |
| 12. | - Analysis of measurement data and preparation of reports | lot | 1 |

- DOCUMENTS TO BE SUBMITTED DURING THE PERFORMANCE OF THE CONTRACT

| No. | TITLE | Submission Time |
| --- | --- | --- |
|  | Final / Comprehensive Measurement Reports | To be submitted within 20 calendar days following completion of the Services. |
|  | Comparative Analysis of Measurements at the Contact Source and site Levels | To be submitted within 20 calendar days following completion of the Services. |

- PLACE OF CONTRACT PERFORMANCE

☒ Floating storage and regasification unit (FSRU) Independence

- ☒ at the KN LNG Terminal, located at 23 Kairių St., Klaipėda, Port Quay No. 157 (no direct access from shore)

- ☒ Onshore pipeline section (14.8 km)

- ☒ Gas Metering Station (54 Birbinčių St., Kiškėnai Village, LT-96223 Klaipėda District Municipality)

- ☒ At the LNG reloading station (19 Burių St., Klaipėda, LT-92276)

- CONTRACT PERFORMANCE ARRANGEMENTS AND TIMEFRAMES

  - Timeframes for the Performance of the Services

7.1.1. Services for conducting an inventory of the vessel’s gas equipment and creating a database of methane leaks must be provided within 1 (one) month from the effective date of the contract.

7.1.2. Contact-based source-level methane leak measurement services at the Buyer’s physical facilities (Terminal, Vessel, Station) must be provided within 1 (one) month of the completion of the inventory of the Vessel’s gas equipment and the creation of the methane leak database.

7.1.3. Site-level methane leak measurement services at the Buyer’s physical facilities (at the Terminal, on the Vessel, along the onshore section of the main gas pipeline, and at the Station) must be provided within 1 (one) month of the completion of the inventory of the Vessel’s gas equipment and the creation of the methane leak database.

7.1.4. Services for analysing the measurement data and preparing reports must be provided within 20 (twenty) calendar days after the completion of all specified source-level and facility-level methane leak measurement services.

  - Ordering Procedure

☒ By e-mail

- 8. RECTIFICATION OF DEFICIENCIES

8.1. Any deficiencies identified during the performance of the Contract shall be corrected within 20 (twenty) business days from the date on which the Buyer sends an e-mail notification to the Supplier regarding improperly performed or non-conforming Services.

- BUYER’S OBLIGATIONS RELATED TO THE PROCUREMENT OBJECT

- 9.1. No later than 2 (two) business days from the effective date of the Contract, the Buyer shall provide the Supplier with detailed information regarding the scope and level of detail of the inventory to be carried out and shall provide the database template.

- ANNEXES

Appendix No. 1. Process Flow Diagrams of Measurement Facilities (CONFIDENTIAL)

This Annex shall be made available to procurement participants who have submitted duly signed confidentiality undertakings upon invitation to submit their initial tenders.