APPROVED

by order No.   of the CEO of AB “Amber Grid” of 29/01/2025

COORDINATED

with National Energy Regulatory Council

24/01/2025

PROCEDURE FOR ASSESSING CONFORMITY OF MARKING OF GIPL TRUNK GAS PIPELINE CONNECTING PARTS

(document identifier 2024:v6)

Content:

Abbreviations used in the Procedure	3

I. Scope of the Procedure	3

II. Scope of inspection of connecting parts	3

III. Selection procedure	4

IV. Other conditions	5

# Abbreviations used in the Procedure

- Selection procedure - the procedure for the selection of the connecting parts based on the random selection method laid down in LST ISO 2859-2:2020 “Sampling procedures for inspection by attributes.  Part 2: Sampling plans indexed by limiting quality (LQ) for isolated lot inspection” by randomly selecting certificates/connecting parts from the Group for inspection, ensuring limiting quality (LQ) of no more than 8%.

- Company/Customer/Contracting Entity - AB “Amber Grid”.

- Expert - a specialist with the necessary knowledge, experience and qualifications (where applicable) engaged by the Service provider.

- GIPL - a gas interconnection between Poland and the Republic of Lithuania, on Lithuanian territory.

- Group - a group of connecting parts established in accordance with the requirements of Chapter III. of the Procedure.

- Connecting parts / Parts - Connecting parts (blinds, elbows, connections, flanges, transitions, tees) installed in the GIPL trunk pipeline.

- Non-conformity - non-conformity of the marking of the Connecting part with the certificate.

- Service provider - the service provider with whom the Customer has concluded an agreement for the assessment of Connecting parts.

- Rules - the Rules for the Installation and Expansion of the Trunk Gas Pipeline approved by the Order of the Minister of Energy of the Republic of Lithuania of 28 January 2014 No. 1-12 “On the Approval of the Rules for the Installation and Expansion of the Trunk Gas Pipeline”.

- Procedure - this procedure for assessing the conformity of the marking of the Connecting parts of the GIPL trunk gas pipeline.

# I. Scope of the Procedure

- The purpose of this Procedure is to determine the selection and marking of Connecting parts and the conformity of the marking on the Connecting parts with the marking specified in the certificates.

- This Procedure sets out the assessment of Connecting parts in accordance with the Rules and other legislation.

# II. Scope of inspection of connecting parts

- In order to assess the compliance of the Connecting parts with the requirements of the Procedure, the following inspections of the Connecting parts shall be carried out in a sequential manner in accordance with the Selection procedure set out in the Procedure:

  - inventory of certificates;

  - assessment of the conformity of the actual marking of the Connecting parts and of the marking indicated in the certificate;

- The sample of Connecting parts to be inspected shall be selected in accordance with the Selection procedure set out in Chapter III of the Procedure.

- The Expert must check the marking of the selected Connecting parts and assess the conformity with the marking indicated in the certificate.

- In the event that it is not possible to determine the interconnection by the marking of the Connecting parts, the Expert must mark the Connecting part as inappropriate or justify the appropriateness by specific provisions of the legislation to show that the lack of interconnection is lawful.

- After inspecting the markings of the selected Connecting parts, the Expert shall draw up a data comparison table in which he/she shall detail the non-conformities or indicate that the Connecting part is suitable (based on the specific requirements of the standard), assess the criticality of the non-conformity and give a final conclusion on conformity.

# III. Selection procedure

- Selection procedure is designed to select the Connecting parts to be inspected in order to ensure an optimal, efficient and objective selection of the sample of Connecting parts to be inspected by means of random sampling.

- Selection procedure based on random sampling according to LST ISO 2859-2:2020.

- Connecting parts shall be grouped into separate control groups by manufacturer.

- The Expert shall select a random sample from the individual control groups for inspection of the marking of the Connecting parts by drawing up a protocol for the separation of the Connecting parts from the control group, signed by the Expert and the Customer.

- Preliminary quantity of Connecting parts and Connecting parts to be inspected:

| Manufacturer | Number of Connecting parts, pcs. | Control group size, pcs. | Quantity of Connecting parts to be inspected by selection procedure, pcs. |
| --- | --- | --- | --- |
| DELCORTE s.a.s. | 141 | 91÷150 | 26 |
| PETROMETAL s.r.o. | 254 | 151÷280 | 28 |
| TASTA ARMATURA Sp. z o.o. | 423 | 281÷500 | 32 |
| S.C. Sara S. R. L. | 12 | 12 | 12 |
| Fitok | 62 | 51÷90 | 24 |
| T.D. Williams | 20 | 16÷25 | 17 |
| In total: | 912 | - | 139 |

- The quantity of Connecting parts may be adjusted after an inventory of the certificates and the quantity of parts to be inspected shall be determined in accordance with the procedures described in the Procedure. The size of the control group may be adjusted if it is determined that the marking of the Part is optional according to the requirements of the applicable standard.

- The Expert shall enter the data in a table after inspecting the marking of the connecting part against the marking specified in the certificate.

| Location of the Connecting part between seams | Type of the Connecting part | Manufacturer of the Connecting part | Compliance/non-compliance (specify discrepancies) | Conclusion |
| --- | --- | --- | --- | --- |
| Seam No.- Seam No. | Tee, elbow, blind, etc. |  | This section describes what markings are on the connecting part and what markings are indicated on the certificate, | The connecting part and the certificate meet/do not meet the legal requirements and can/cannot be used safely for its intended purpose. Indicating non-conformities, if any, in relation to the design of the connecting part and the requirements of the normative legislation. |

- The Expert, by signing the table, guarantees and declares that the inspection information contained in the table is objective, correct and in accordance with the provisions of the normative legislation.

## IV. Other conditions

- The Service provider shall, after the signature of the agreement, provide a detailed timetable for the performance of the services, which shall reflect all the stages of the inspection referred to in Chapter II of the Procedure.

- At least twice a month, the Service provider shall, in agreement with the Customer, organise a meeting with the Customer on the progress and results of the interim assessment of the Connecting parts. The meeting may be conducted remotely or at the Customer's premises.

- After the final assessment of the Connecting parts has been prepared and submitted to the Customer, the Service provider shall arrange for the results of the assessment of the Connecting parts to be presented to the Customer remotely or at the Customer's premises within a maximum of 7 calendar days.

- The final assessment of the Connecting parts must be submitted in Lithuanian in electronic (Word and/or Excel and/or PowerPoint and Adobe Acrobat Reader) formats. The final assessment submitted must be signed electronically by the Service provider and the Expert.

- A representative of the Service provider shall, at the invitation of the Customer, present the final results of the assessment of the Connecting parts to the authorities concerned at a time agreed between the Parties.

_____________________________