TECHNICAL SPECIFICATION

- DEFINITIONS AND ABBREVIATIONS

  - Order – a written document submitted to the Service Provider on the basis of the Contract by text message, e-mail and/or through the information system specified by the Purchaser, indicating the quantities of the Services, delivery addresses and delivery deadline.

  - Related Services – services that are not specified in the Technical Specification but are related to the Subject of Procurement. The total value of such Related Services shall not exceed 10% of the Initial Contract Value.

  - Mobilization – arrival at and departure from the address specified in Section 3 of the Technical Specification, including travel, accommodation and other related expenses.

- CHARACTERISTICS AND SCOPE OF THE SUBJECT OF PROCUREMENT

2.1. Boiler Expert Assessment.

2.2. The quantities of the Services are provided in the table below:

| No. | Description | Unit of Measure | Estimated Quantity |
| --- | --- | --- | --- |
| 1. | Boiler assessment expert at the Purchaser’s Site | Hour | 200 |
| 2. | Boiler assessment expert, remote work | Hour | 200 |
| 3. | Boiler assessment expert, travel time | Hour | 50 |
| 4. | Boiler assessment expert, Mobilization | Unit | 9 |
| 5. | Measurement using an ash chemical composition probe | Unit | 1 |
| 6. | Measurement using a temperature gradient probe | Unit | 1 |
| 7. | Mobile high-resolution air-cooled camera probe | Working day | 1 |

Description of the Subject of Procurement

  - The expert at the Purchaser’s Site shall perform the following:

    - First Boiler Pass.
Carry out a visual inspection of the boiler refractory lining, a visual inspection of the boiler waterwall tube cladding (Inconel), and electromagnetic testing at identified critical locations.

    - Second and Third Boiler Passes.
Carry out a visual inspection of the tubes and ultrasonic testing at identified critical locations.

    - Superheaters.
Carry out a visual inspection of the tubes and ultrasonic testing at identified critical locations. Perform a visual inspection of the superheater tube cladding (Inconel) and electromagnetic testing at identified critical locations.

    - Boiler Economizer.
Carry out a visual inspection of the tubes and ultrasonic testing at identified critical locations.

    - Flue Gas Cleaning Equipment.
Carry out a visual inspection and identify corrosion areas without performing ultrasonic testing.

  - Expert’s remote work.
Prepare an expert assessment report indicating the assessment findings. The Purchaser shall provide additional technical documentation of the equipment. Comments shall be presented in visual form (with photographs), describing each inspected location separately. Indicate possible causes of the damage, its potential progression and characteristics. Provide conclusions and recommendations for damage elimination, localization, and equipment operation.

  - Expert’s Mobilization.
Mobilization includes travel, accommodation, taxi or ride-hailing services, car rental, and other organizational expenses related to travel.

  - The Purchaser anticipates that the Services may be required on non-working days or public holidays, as well as outside the Purchaser’s working hours.

  - Upon completion of the Services, an expert assessment report shall be submitted.

  - Ash chemical composition probe.
It shall ensure isokinetic extraction of flue gas particles. The sampling interval shall be from 30 to 60 minutes, depending on the particle load. The chemical composition of the extracted flue gas particles shall be analyzed.

  - Temperature gradient probe.
It shall be made from a boiler tube. It shall have an internal tube for air cooling. It shall be capable of ensuring a constant temperature profile and recording temperature signals (from 5 to 10) with remote monitoring capability.

  - Mobile high-resolution air-cooled camera probe. During boiler operation, it shall be possible to record video inside the boiler, including the first pass (temperature approximately 1000°C). The resolution shall be sufficient to observe the spray patterns of the boiler washing system.

3. PLACE, PROCEDURE AND TIME LIMITS FOR THE PROVISION OF SERVICES

  - The Services shall be provided at: Kauno kogeneracinė jėgainė, UAB, Jėgainės g. 6, Biruliškių k., Kaunas District.

  - The Services shall be provided only on the basis of separate Orders submitted by the Purchaser during the term of the Contract.

  - The Services shall be provided within the time limits specified in the Order. The Service provision period may range from 1 hour to 30 (thirty) calendar days.

  - he Boiler Expert Assessment Services specified in Clause 2.3 shall be provided no later than within 30 (thirty) days from the date of submission of the Order to the Service Provider at the Purchaser’s address: UAB Kauno kogeneracinė jėgainė, Jėgainės g. 6, Biruliškių k., Kaunas District. In accordance with Clause 2.6 of the Technical Specification, the Services may be provided during and outside the Purchaser’s working hours, as well as on public holidays (Working hours: Monday-Thursday 7:30-16:30, Friday 7:30-15:15).

  - The expert assessment report shall be submitted to the Purchaser no later than within 30 (thirty) days from completion of the expert boiler assessment.

  - The Services shall be provided in accordance with the procedure set out in this Technical Specification.

  - The following documents shall be submitted together with the Services:

    - Boiler expert assessment report in English, in PDF format.

4. OTHER REQUIREMENTS

4.1. Defects of the Services and/or of the Service Result shall mean non-compliance with the requirements of the Technical Specification and legal acts regulating the quality of the Services.

4.2. The Client shall have the right to apply to the Service Provider for the rectification of Defects of the Services and/or the Service Result no later than within 10 (ten) days from the date of signing of the Service acceptance certificate / the date of identification of the Defects.

4.3. A period of 10 (ten) days shall be established for the rectification of Defects of the Service Result identified by the Client