TECHNICAL SPECIFICATION

- TERMS AND ABBREVIATIONS

  - Buyer – UAB "Ignitis".

  - Supplier – an economic entity – a natural person, private legal entity, public legal entity, other organizations and their divisions, or a group of such persons, with whom the Buyer enters into a Contract.

  - Contract – the agreement concluded between the Supplier and the Buyer regarding the object of Purchase

  - Goods – Battery Energy Storage System (BESS).

  - Services – Maintenance of Goods during their operation throughout the validity period of the Contract.

  - Order – A written document provided to the Supplier via email on the basis of the Contract, specifying the quantities of Goods and/or Services ordered, delivery or service provision addresses, and the deadline.

  - Buyer's working hours – working hours calculated during the Buyer's working time: Monday to Thursday from 7:30 AM to 4:30 PM, Friday from 7:30 AM to 3:15 PM.

- SUBJECT OF THE PROCUREMENT

  - Battery Energy Storage System (BESS) and maintenance services during their operation.

- SCOPE OF THE PROCUMENT

  - The quantities of Goods and Services are provided in Tables No. 1 and No. 2 below:

Lentelė Nr. 1

| No. | Name | Quantity, units |
| --- | --- | --- |
| 1. | Battery Energy Storage System (BESS) | 1 |

Lentelė Nr. 2

| No. | Name | Description | Maximum quantity, working hours |
| --- | --- | --- | --- |
| 1. | Corrective Maintenance (CM) | Unscheduled repairs and fault rectification | 120 |
| 2. | Auxiliary sytems (Aux_syst) | Inspection and maintenance of auxiliary systems | 72 |
| 3. | Training & Technical Support (TTS) | On-site or remote training for operators and engineers | 120 |
| 4. | Technical Support During Grid Code Compliance Testing (GST) | Including but not limited to mFRR, aFRR, and FCR functionalities, remote assistance, system configuration, troubleshooting, and coordination with the relevant DSO/TSO representatives. | 48 |

- PLACE OF PERFORMANCE OF CONTRACTUAL OBLIGATIONS

4.1. The Goods must be delivered and the maintenance services provided at the following addresses: Stasylų g. 21, LT-02244 Vilnius, Lithuania or Vejukų k. 5, 60358 Vejukai, Viduklės sen., Raseiniai district municipality.

- REQUIREMENTS FOR THE OBJECT OF PURCHASE

## 5.1.The requirements for the Battery Energy Storage System (BESS) are specified in Table No. 3.

## Table No. 3

|  | Description | Requirement |
| --- | --- | --- |
|  | General Specification |  |
|  | Nameplate Power Output | 1500-1550 kW |
|  | Nameplate power distribution through connection points | ≤525 kW |
|  | Usable Energy Capacity and Depth of Discharge (DOD) | ≥3000 kWh (2-hour discharge duration) |
|  | Application | Commercial use, AC-coupled |
|  | Installation site | Floor installation, outdoor |
|  | Cooling method | Liquid cooling |
|  | Battery system |  |
|  | Battery Cell Chemistry | Lithium Iron Phosphate (LiFePO₄ / LFP) |
|  | Battery Configuration | Modular, scalable design with integrated Battery Management System (BMS) |
|  | Charging/Discharging rate | 0.5C |
|  | Cycle Life | ≥6,000 full cycles |
|  | Product warranty | ≥5 years (60 months) |
|  | Performance warranty | ≥10 years (120 months) |
|  | Operating temperature | from -25°C to +50°C |
|  | Full capacity operating ambient temperature in absence of power deration (0.5C). | from -10°C to +30°C |
|  | Round-trip efficiency at PCS (AC terminals) | ≥83 % |
|  | Upon successful completion of commissioning, the Supplier shall provide a Warranty Completion Certificate, confirming that the system has been tested, configured, and is operating in accordance with the technical specifications and warranty terms. |  |
|  | Power Conversion system |  |
|  | Nomical Grid Voltage/Frequency | 400 Vac/50 Hz |
|  | Power Factor Range | ≥±0.9 adjustable |
|  | Noise emission | ≤80 dB |
|  | Power Conversion System (PCS) | Integrated internally |
|  | Input Method | AC bottom entry |
|  | Islanding mode support | Available |
|  | Backup power |  |
|  | Backup mode | Yes |
|  | Automatic Transfer Switch (ATS) | Integrated or compatible. |
|  | Load Prioritization | Configurable critical load support. |
|  | Island Mode Operation | Capable of operating independently from the grid. |
|  | Reconnection time | ≤ 20ms |
|  | Switchgear nominal output power | ≥800 kW |
|  | Switchgearominal grid Voltage | 400V |
|  | On-load switching power | ≥475 kW |
|  | Control & Communication |  |
|  | Communication Protocols | Modbus TCP/IP, RS485, CAN, optional OPC-UA |
|  | SCADA/BMS/EMS Integration | Compatible with external EMS, supports open APIs |
|  | Cybersecurity | Role-based access control, encrypted communication (TLS/SSL) |
|  | EMS Compatibility | Supports integration with third-party EMS platforms |
|  | Enclosure & Safety |  |
|  | Protection level | ≥ IP54 |
|  | Corrosion protection class | ≥ C3 |
|  | Fire Suppression System | Built-in or compatible with external system fire suppression system with integrated over-heating detection, heat sensors and combustible gas detection. |
|  | Maintenance & Support |  |
|  | The Contractor shall ensure that qualified Operation and Maintenance (O&M) personnel are based within the European Union (EU), with the capability to be deployed on-site |  |
|  | Training | On-site/off-site training for operation and maintenance staff after site commissioning. |
|  | Documentation | Full O&M manuals, wiring diagrams, factory test results and commissioning reports availability in English or Lithuanian language. |
|  | 1st group: Response time for critical faults, i.e., , fire risk, major safety hazard/resolution time | ≤ 2 working hours/≤8 working hours. Penalty would be applied if resolution time exceeds 1 day. |
|  | 2nd group: Response time for major faults, i.e., system shutdown, grid disconnection, significant performance degradation, PCS or battery subsystem failure/resolution time | ≤ 4 working hours/≤24 working hours. Total time should not exceed 2 weeks. |
|  | 3rd group: Response time for minor faults, i.e., all other defects that are not covered by 1st and 2nd group. (e.g., HVAC, lighting) /resolution time | ≤ 24 working hours/≤72 working hours. Total time should not exceed 12 weeks/year |
|  | The response and resolution times defined in Sections 7.4–7.6 shall be measured in accordance with the following principles: All incident notifications shall be submitted by the Buyer to the Supplier via email, which shall serve as the official record of notification. The response and resolution time countdown shall begin from the timestamp of the Supplier’s receipt of this email. If a notice is submitted outside of the Buyer's working hours, the time calculation begins on the next working day at 7:30 AM. Upon receiving the notification, the Supplier shall provide an initial reaction, consisting of an email acknowledgement confirming that the issue has been logged, the preliminary classification (critical, major, or minor), and the planned method of intervention (remote or on-site). This acknowledgement must be issued within the applicable response time limits defined in Sections 7.4–7.6. The supplier's liability for failure to fulfill maintenance and support obligations during the warranty period and the procedure for calculating penalties are discussed in detail in Clause SD 6.5 of the Agreement. |  |
|  | Certifications |  |
|  | UL 9540 / UL 9540A (thermal runaway), IEC 62619 (cell and module), CE, FCC, or equivalent national safety certification, ISO 27001 |  |
|  | Balancing/DSO criterias |  |
|  | Technical requirements are indicated in Annexes no. aFRR, mFRR, FCR, DSO. These annexes define the technical and procedural requirements for Battery Energy Storage Systems (BESS) to qualify and operate in Lithuania’s (FCR), (aFRR), and (mFRR) markets, aligned with Baltic LFC reserve prequalification principles and ensuring safe and compliant integration into the distribution network. |  |

Connection diagram is indicated in Technical specification Annex No.1

5.2. The list of documents required to be submitted is specified in Table No. 4.

Table No. 4

|  | Required document list |
| --- | --- |
| No | Type of document |
|  | Communication and network topology management architecture/schematic view |
|  | Specifications for auxiliary systems, including HVAC, fire suppression, lighting, grounding, protection relays, and auxiliary power supply system’s necessary to support safe, reliable, and continuous operation of the BESS under all operating conditions |
|  | The supplier shall ensure the availability of all critical spare parts within the European Union. A comprehensive spare parts pricelist shall be provided, including part quantity, descriptions, unit prices, and lead times. A recommended list of spare parts to be stored on-site shall also be submitted, specifying minimum stock levels for each item (based on system criticality and failure rate), quantities and unit prices, storage and handling requirements. |
|  | The Battery Energy Storage System (BESS) shall be equipped with an Energy Management System (EMS) that supports full integration with external control and monitoring systems. The supplier shall provide a complete signal list document, detailing all input/output signals, data points, and control commands. This document must include signal names, types, units, scaling factors, and update rates. |
|  | The supplier shall provide warranty terms and conditions for all major components of the BESS, Operational manuals for installation, commissioning, and maintenance, technical datasheets for all key components, and battery degradation curves, indicating expected performance over time under standard operating conditions. |
|  | The BESS shall include a backup power supply system to maintain battery temperature within the specified operating range during grid outages or system shutdowns. If the battery system is capable of self-heating without the need for auxiliary power, this functionality must be clearly documented, including operational limits and activation conditions. The supplier shall specify all related requirements, including power source, control logic, and system components necessary to ensure uninterrupted thermal management. |
|  | BESS Pre-Commissioning Installation Requirements Checklist |
|  | UL 9540 / UL 9540A (thermal runaway), IEC 62619 (cell and module), CE, FCC, or equivalent national safety certification, ISO 27001 |

5.2.1. The Supplier must provide the Buyer with the documents specified in Table No. 4 of the Technical Specifications no later than within 7 (seven) days from the effective date of the Contract.

5.3. Additional Requirements for Service Provision:

5.3.1. Minimum Billable Time. The minimum billable time per intervention is 1 (one) hour. Additional time is billed in 0.5-hour increments.

5.3.2. Service Reports. Each intervention must be accompanied by a work report (scope, start/end times, personnel, conclusions, materials used). Buyer's approval is necessary for invoice validation.

5.3.3. The maximum quantity specified in Table No. 2 of the Technical Specifications can be ordered as needed during the Contract period, with the specific quantity indicated at the Buyer's initiative. However, in all cases, the purchased quantity cannot exceed the total Contract price. The Buyer is not obligated to purchase the entire specified quantity or any portion thereof.

- DELIVERY PROCEDURE AND SERVICE PROVISION TERMS

  - The goods must be delivered no later than 180 (one hundred eighty) days from the day the Order is submitted to the Supplier. The goods order must be placed no later than 30 (thirty) days from the effective date of the Contract. Services are purchased as needed and only according to separate Orders from the Buyer during the validity of the Contract.

  - Services are purchased as needed and only according to individual Buyer Orders during the term of the Contract

  - The Supplier must deliver the Goods and provide Services at the address specified in Section 4 of the Technical Specification during the Buyer's working hours (Monday-Thursday 7:30 AM – 4:30 PM, Friday 7:30 AM – 3:15 PM).

  - The Goods and/or Services will be purchased and must be supplied/provided in accordance with the procedure established in this Technical Specification.

  - The services must be provided no later than the deadline specified in the Order.

  - Warranty service times are specified in Section 5 of this Technical Specification.

- ATTACHMENTS

  - Annex No. 1 DGR Principal connection diagram

  - Annex No. 2 Confirmation of Readiness for Automatic Frequency Restoration Reserve Services (aFRR)

  - Annex No. 3 Protocol for Coordination of Power Plant RAA with DSO

  - Annex No. 4 Confirmation of Readiness for Frequency Containment Reserve Services (FCR)

  - Annex No. 5 Confirmation of Readiness for Manual Frequency Restoration Reserve Services (mFRR)

Three (3) seperated connection point at AC side

After 6000 cycles, the SOH has to be ≥60%.

FCR is a fast, decentralized response to frequency deviations. Providers must ensure symmetrical response within ±200 mHz and full activation within 30 seconds. LER (Limited Energy Reserve) providers must guarantee 30 minutes of full activation in alert states. Real-time data exchange and SOC (State of Charge) monitoring are mandatory. Strict voltage/frequency tolerance and ROCOF (Rate of Change of Frequency) immunity are required.

aFRR is centrally activated via the PICASSO platform with a control signal every 1–10 seconds. Full activation time (FAT) must not exceed 5 minutes. Providers must support real-time telemetry, energy reservoir management (ERM), and meet accuracy and availability standards. Grouped units (RPGs) are allowed with specific data aggregation and activation rules.

mFRR is manually activated by the TSO with FAT ≤ 12.5 minutes and start time ≤ 7 minutes. Providers must respond to activation instructions and maintain power setpoints. LER mFRR providers must describe ERM strategies and ensure energy availability. XML-based data exchange and bid submission follow ENTSO-E CIM standards.

This annex outlines the RAA (Remote Automation and Adjustment) tuning protocol for Type B power plants, in accordance with DSO's conformity assessment rules. It details the procedures for verifying current, voltage, and frequency protection settings, as well as automation and reactive power control functionalities. The protocol includes requirements for documentation, visual evidence of settings, and compliance with EN 50549 and EU Regulation 2016/631. It also specifies the roles of the power plant contractor and DSO representatives in the inspection and approval process, ensuring safe and compliant integration into the distribution network.