PROCUREMENT TENDER: (2025-IGN-184) BATTERY ENERGY STORAGE SYSTEM (BESS) AND MAINTENANCE SERVICES DURING OPERATION

## LEGAL ENTITY SUBMITING THE TENDER

| Name(s) of the Supplier/Members of the Supplier Group |  |
| --- | --- |
| Details of the contact person authorised to liaise directly during the procurement procedure (name, surname, phone number, e-mail). |  |

## INFORMATION ABOUT THE OFFERED GOODS, SERVICES OR WORK

Information on the offered goods, services or work and other information in the tender, shall be provided by completing the annexes to the tender referred to in Section 6 and by attaching the specified documents.

(fill in the annexes to the tender and attach the documents)

## TENDER PRICE

The tender price and its components shall be indicated in the Annex to the Tender ‘Tender Price’.

(fill in the annex to the tender)

## SUBCONTRACTING

The lot of the Contract transferred to the subcontractors (you must indicate all the elements the subcontractors will be engaged for (even if specific subcontractors are not known at the time of submission of the tender). Additional subcontractors which will be engaged for and/or the lot of the procurement contract the subcontractors will be engaged for, which were not specified in the supplier‘s application, are indicated in the table.

(fill in the table)

| No. | Subcontractor's name (if known) | Country or territory of registration of the subcontractor (for a natural person, indicate their permanent place of residence (country) and nationality) | The lot of the procurement contract the subcontractors will be engaged for |
| --- | --- | --- | --- |
| 1 | 2 | 3 | 4 |
| E.g. | UAB “AAA” | Lithuania | Goods installation work |

## CONFIDENCIAL INFORMATION

Confidential information is included in the tender (including annexes and attached documents			☐ No	☐ Yes

## ANNEXES AND DOCUMENTS ATTACHED TO THE TENDER

The following annexes shall be submitted together with the tender and shall be considered an integral part of the tender:

- Compliance with technical requirements;

- Country of manufacture of the offered goods;

- Supplier's declaration of origin;

- Tender price;

- Declaration of Conformity with National Security Requirements;

- Life-cycle costs

- The following documents shall be attached to the tender and shall be considered an integral part of the tender:

- The documents defining the technical and qualitative characteristics of offered goods (documents are provided to substantiate compliance with the parameters specified in points 1-6 of Table No. 3 of the Technical Specification).

- A free-form declaration confirming that the offered goods are equivalent, compatible with the equipment owned by the Buyer and guarantee full indemnification for the Buyer in the event where the goods offered by the supplier cause damage to the equipment and/or facilities used by the Buyer; (if equivalent goods are offered)

- A valid written mandate or other document authorising the signing of the tender; (if the tender is signed by a person other than the CEO)

- The documents demonstrating the requirements set out in the Annex to the SPC ‘Requirements for Contribution to Sustainability and Resilience;

## REPRESENTATIONS

By submitting a tender, I confirm that:

- I have examined all the terms and conditions of the procurement;

- I offer the goods, services or work specified in the procurement documents together with this tender, which includes technical and financial information defined in the specified and submitted annexes to the tender;

- as a professional procurement participant, I act in compliance with the requirements of the effective and applicable legislation in the Republic of Lithuania, even if these requirements are not directly stated in the procurement documents, and I understand my obligations and responsibilities;

- by signing this tender, I confirm the authenticity of all the annexes, documents and data submitted with the tender;

_______________________________________________________

(Position, name, surname and signature of the person authorised by the supplier)

Annex to tender

COMPLIANCE WITH THE REQUIREMENTS OF THE TECHNICAL SPECIFICATION

| No. | Requirement set out in the technical specification | Required amount, condition | Specific parameter of the offered product | Reference to the following submitted with the tender: - documents (document type, page or specific location in the document) supporting the parameter of the offered product; or - publicly available information (a specific website link with an explanation where to find the requested information) |
| --- | --- | --- | --- | --- |
| 1 | 2 |  | 3 | 4 |
| E.g.: | Length | not exceeding 180 cm | Length – 178 cm | Table description, page 5. |
|  | Product manufacturer, type, model |  |  |  |
|  | General Specification |  |  |  |
| 1.1. | Nameplate Power Output | 1500-1550 kW |  |  |
| 1.2. | Nameplate power distribution through connection points | ≤525 kW |  |  |
| 1.3. | Usable Energy Capacity and Depth of Discharge (DOD) | ≥3000 kWh (2-hour discharge duration) |  |  |
| 1.4. | Application | Commercial use, AC-coupled |  |  |
| 1.5. | Installation site | Floor installation, outdoor |  |  |
| 1.6. | Cooling method | Liquid cooling |  |  |
|  | Battery system |  |  |  |
| 2.1. | Battery Cell Chemistry | Lithium Iron Phosphate (LiFePO₄ / LFP) |  |  |
| 2.2. | Battery Configuration | Modular, scalable design with integrated Battery Management System (BMS) |  |  |
| 2.3. | Charging/Discharging rate | 0.5C |  |  |
| 2.4. | Cycle Life | ≥6,000 full cycles |  |  |
| 2.5. | Product warranty | ≥5 years (60 months) |  |  |
| 2.6. | Performance warranty | ≥10 years (120 months) |  |  |
| 2.7. | Operating temperature | from -25°C to +50°C |  |  |
| 2.8. | Full capacity operating ambient temperature in absence of power deration (0.5C). | from -10°C to +30°C |  |  |
| 2.9. | Round-trip efficiency at PCS (AC terminals) | ≥83% |  |  |
| 3. | Power Conversion system |  |  |  |
| 3.1 | Nomical Grid Voltage/Frequency | 400 Vac/50 Hz |  |  |
| 3.2. | Power Factor Range | ≥±0.9 adjustable |  |  |
| 3.3 | Noise emission | ≤80 dB |  |  |
| 3.4 | Power Conversion System (PCS) | Integrated internally |  |  |
| 3.5. | Input Method | AC bottom entry |  |  |
| 3.6. | Islanding mode support | Available |  |  |
| 4. | Backup power |  |  |  |
| 4.1. | Backup mode | Yes |  |  |
| 4.2. | Automatic Transfer Switch (ATS) | Integrated or compatible. |  |  |
| 4.3. | Load Prioritization | Configurable critical load support. |  |  |
| 4.4 | Island Mode Operation | Capable of operating independently from the grid. |  |  |
| 4.5. | Reconnection time | ≤ 20ms |  |  |
| 4.6. | Switchgear nominal output power | ≥800 kW |  |  |
| 4.7. | Switchgearominal grid Voltage | 400V |  |  |
| 4.8. | On-load switching power | ≥475 kW |  |  |
| 5. | Control & Communication |  |  |  |
| 5.1 | Communication Protocols | Modbus TCP/IP, RS485, CAN, optional OPC-UA |  |  |
| 5.2. | SCADA/BMS/EMS Integration | Compatible with external EMS, supports open APIs |  |  |
| 5.3. | Cybersecurity | Role-based access control, encrypted communication (TLS/SSL) |  |  |
| 5.4. | EMS Compatibility | Supports integration with third-party EMS platforms |  |  |
| 6. | ENCLOSURE & SAFETY |  |  |  |
| 6.1. | Protection level | ≥ IP54 |  |  |
| 6.2. | Corrosion protection class | ≥ C3 |  |  |
| 6.3. | Fire Suppression System | Built-in or compatible with external system fire suppression system with integrated over-heating detection, heat sensors and combustible gas detection. |  |  |

|  | Mandatory Technical Documentation Checklist for BESS Compliance Verification |  |  |
| --- | --- | --- | --- |
| No | Type of document | Compliance with the criteria (mark the suitable box ☒) |  |
|  |  | Yes | No |
|  | Communication and network topology management architecture/schematic view | ☐ | ☐ |
|  | Specifications for auxiliary systems, including HVAC, fire suppression, lighting, grounding, protection relays, and auxiliary power supply systems necessary to support safe, reliable, and continuous operation of the BESS under all operating conditions | ☐ | ☐ |
|  | The supplier shall ensure the availability of all critical spare parts within the European Union. A comprehensive spare parts pricelist shall be provided, including part quanity, descriptions, unit prices, and lead times. A recommended list of spare parts to be stored on-site shall also be submitted, specifying minimum stock levels for each item (based on system criticality and failure rate),quantities and unit prices, storage and handling requirements. | ☐ | ☐ |
|  | The Battery Energy Storage System (BESS) shall be equipped with an Energy Management System (EMS) that supports full integration with external control and monitoring systems. The supplier shall provide a complete signal list document, detailing all input/output signals, data points, and control commands. This document must include signal names, types, units, scaling factors, and update rates. | ☐ | ☐ |
|  | The supplier shall provide warranty terms and conditions for all major components of the BESS, Operational manuals for installation, commissioning, and maintenance, technical datasheets for all key components, and battery degradation curves, indicating expected performance over time under standard operating conditions. | ☐ | ☐ |
|  | The BESS shall include a backup power supply system to maintain battery temperature within the specified operating range during grid outages or system shutdowns. If the battery system is capable of self-heating without the need for auxiliary power, this functionality must be clearly documented, including operational limits and activation conditions. The supplier shall specify all related requirements, including power source, control logic, and system components necessary to ensure uninterrupted thermal management. | ☐ | ☐ |
|  | BESS Pre-Commissioning Installation Requirements Checklist | ☐ | ☐ |
|  | UL 9540 / UL 9540A (thermal runaway), IEC 62619 (cell and module), CE, FCC, or equivalent national safety certification, ISO 27001 | ☐ | ☐ |

Annex to tender

COUNTRY OF MANUFACTURE OF THE OFFERED GOODS

(in accordance with Article 67 of the LP)

The following origin of the offered goods:

(choose one of the options)

☐ the offered goods are manufactured in the countries of the European Union (hereinafter – EU) and/or in the countries that have concluded the World Trade Organization Agreement on Government Procurement (checked here).

☐ all/part of the offered goods are manufactured in non-EU countries and/or in the countries that have not concluded the World Trade Organization Agreement on Government Procurement. (if this option is selected, the information for these goods must be provided in the table below)

| Name of the goods | Manufacturer | Country of origin* | Value of the goods as a percentage of the value of the goods in the tender ** |
| --- | --- | --- | --- |
| 1 | 2 | 3 | 4 |
| E.g.: Transformer YYY | E.g.: Spooz | E.g.: North Korea | E.g.: 25% |

* Please note that when assessing the compliance of the countries listed in the table with the requirements of Article 67(1) of the LP, consideration will be given to whether the country has concluded a multilateral or bilateral agreement with the EU that ensures competitive and effective access for EU companies to those countries’ public procurement markets. Information on countries that have concluded multilateral or bilateral agreements with the EU can be found here; however, it is essential to verify that the agreement covers access to public procurement markets.

**The percentage of the value of the goods is calculated based on the price of the offered goods, not on their cost. When procuring goods and services, the table should only show the value of the goods in relation to the total value of the offered goods, not the total price of the offered goods and services.

Annex to tender

COUNTRY OF ORIGIN AND VALUE OF THE COMPONENTS OF THE OFFERED GOODS

| Subcategory of Zero-Balance Technologies | Final Products | Main specific components | Country of origin | Component price(Value), EUR excl. VAT | Component's Value Share in the Final Product (%) |
| --- | --- | --- | --- | --- | --- |
| Battery technology | Fina Battery Energy Storage System | Complete batteries |  |  |  |
|  |  | Battery modules |  |  |  |
|  |  | Battery cells |  |  |  |
|  |  | Battery management systems |  |  |  |
|  |  | Battery thermal management systems |  |  |  |
| Total value in EUR excluding* VAT |  |  |  |  |  |

When determining the value share, country of origin, and other related circumstances of the proposed zero-balance technology or its key specific components supplied within the European Union, the definitions and conditions set out in the Climate Neutral Industry Act (NZIA regulation), the Regulation (EU) No 952/2013 of the European Parliament and of the Council of 9 October 2013, and/or other legislative acts adopted by the European Union that are in effect at the time of the publication of the Procurement conditions are followed.

*The value is calculated based on the price of the proposed Battery Energy Storage System (BESS) indicated in line 1 of the appendix "Offer Price." If goods and services are being purchased, the table should only reflect the value of the goods from the total proposed value of goods, not from the total combined price of goods and services offered.

Note: During the procurement process, the Buyer may request the Supplier to provide documents verifying the accuracy of the submitted information.

Annex to tender

SUPPLIER’S DECLARATION OF ORIGIN

(PURSUANT TO THE ART. 45 (21) OF THE LPP / ART. 58 (41) OF THE LP)

__ ______ 202_

I, full name and title of the CEO of the Supplier or the person authorised by him/her, confirm that Supplier name I manage (represent), which participates in the procurement conducted by UAB “Ignitis grupės paslaugų centras”, complies with the following requirements:

- The Supplier, its subcontractor, economic entities whose capacities it relies on, the manufacturer of the goods (including their components and packaging) offered by the Supplier or the persons controlling them are not registered in (or, if the Supplier, its subcontractor, economic entities whose capacities it relies on, the manufacturer of the goods or the person controlling them, is a permanent resident or have the nationality of) the territories of the Russian Federation, the Republic of Belarus, Crimea annexed by the Russian Federation, the territories of Transnistria not under the control of the Government of the Republic of Moldova, the territories of Abkhazia and South Ossetia not under the control of the Government of the Republic of Sakartvelo.

- The offered Goods (including their components and packaging) are not manufactured in the territories of the Russian Federation, the Republic of Belarus, Crimea annexed by the Russian Federation, the territories of Transnistria not under the control of the Government of the Republic of Moldova, the territories of Abkhazia and South Ossetia not under the control of the Government of the Republic of Sakartvelo.

- The procured services will not be rendered from the Russian Federation, territories of the Republic of Belarus, Crimea annexed by the Russian Federation, the territories of Transnistria not under the control of the Government of the Republic of Moldova, the territories of Abkhazia and South Ossetia not under the control of the Government of the Republic of Sakartvelo.

- the Supplier, its subcontractors and economic entities whose capacities it relies on do not conduct business in the territories of the Russian Federation, the Republic of Belarus, Crimea annexed by the Russian Federation, the territories of Transnistria not under the control of the Government of the Republic of Moldova, the territories of Abkhazia and South Ossetia not under the control of the Government of the Republic of Sakartvelo, or are not participants or managers, other type of members of the management or supervisory body of a group of economic entities with at least one member conducting business in the countries or territories referred to above, including any other person(s) who has/have the power to represent the Supplier, subcontractor or economic entity whose capacities are relied on, control it, make a decision on its behalf, enter into a transaction, and thus is involved in the business of such groups of economic entities and/or economic entities.

I hereby confirm that the presented data is accurate and relevant at the date of submission of the tender.

I understand that, if the tender will be recognised as successful based on the evaluation results, the Procuring Entity, in accordance with Article 45(5) of the LPP, Article 58(42) of the LP, may request at any time during the procurement process to submit all or a part of the documents confirming the compliance with the requirements of Article 45(21) of the LPP, Article 58(41) of the LP, provided that they are necessary to ensure the proper conduct of the procurement procedure.

_______________________________________________________

(Position, name, surname and signature of the person authorised by the supplier)

Annex to tender

______________________________________________________________________

(name of the Supplier)

UAB “Ignitis grupės paslaugų centras“

(addressee (name of the contacting authority / contracting entity)

DECLARATION OF CONFORMITY WITH NATIONAL SECURITY REQUIREMENTS

__ ______ 202_ No. __

_______________

(Place of conclusion)

I, __________________________________________________________________________________,

(position and full name of the Head of the Supplier or the authorised person thereof)

do hereby confirm that the company I manage (represent) ____________________________________,

(name of the Supplier)

participating in ______________________________________________________________________

(name of the procurement object, procurement number, date of procurement announcement in CPP IS)

conducted by _______________UAB “Ignitis grupės paslaugų centras“__________________________,

(name of the contracting authority/ contracting entity)

conforms with the following requirements:

| ☐ | the goods offered by the Supplier do not pose a threat to national security – in accordance with Article 37 (9)(1) of the LPP / Article 50(9)(1) of the LP, the manufacturer of the goods or the person controlling it are not registered (if the manufacturer or the person controlling it is a natural person – permanently residing or holding citizenship) in the states or territories specified in the list provided for in Article 92(14) of the LPP. (clause 14.2. (b) of the GPC) |
| --- | --- |
| ☐ | the services offered by the Supplier do not pose a threat to national security – in accordance with Article 37 (9)(2) of the LPP / Article 50(9)(2) of the LP, the provision of services will not be carried out from the states or territories specified in the list provided for in Article 92(14) of the LPP. (clause 14.2. (c) of the GPC) |
| ☐ | the Supplier does not have interests that could pose a threat to national security – in accordance with Article 47(9) of the LPP, the Supplier itself, the subcontractors or economic entities it has engaged or the persons controlling them are not registered (if the Supplier, the subcontractors or economic entities it has engaged or the persons controlling them are natural persons – permanently residing or holding citizenship) in the states or territories specified in the list provided for in Article 92(14) of the LPP. (clause 14.2. (a) of the GPC) |

I hereby confirm that this information is correct and relevant at the date of submission of the tender.

I understand that, in accordance with Article 39 (4) of the LPP, Article 52(4) of the LP, the contracting authority / contracting entity may, at any time during the procurement procedure, request candidates or tenderers to submit all or part of the documents confirming the conformity with Article 37(9) of the LPP, Article 50(9) of the LP, where it is necessary to ensure the proper performance of the procurement procedures.

I understand that, if the tender is recognized as the successful tender according to the results of the evaluation, the documents confirming conformity with national security requirements specified by the contracting authority / contracting entity will have to be submitted.

_____________________________________________________

(Position, name, surname and signature of the Supplier or the authorised person thereof)

Annex to tender

PROPOSED LIFE CYCLE COST PARAMETERS

|  | Abbreviations | Unit | Name of input | Explanation of Input Parameters | Input value |
| --- | --- | --- | --- | --- | --- |
|  | Cap_BESS | kWh | BESS capacity | Total usable energy capacity of the Battery Energy Storage System in kilowatt‑hours (kWh). This is the nominal energy rating of the system, typically at the beginning of life (BOL) |  |
|  | CAPEX_Hardware | Eur | CAPEX BESS | Total capital expenditure for BESS hardware only: battery racks/modules, inverters, PCS, EMS, BMS, transformers, protections, containers/enclosures, cooling/ HVAC, fire suppression, cabling inside enclosure, control equipment. |  |
|  | CAPEX_comm | Eur | CAPEX commissioning | Cost of commissioning and configuration, if the procedure is carried out by the manufacturer or its authorized partners. |  |
|  | CAPEX_total | € | CAPEX (BESS + installation) | This value is calculated automatically as: CAPEX_Hardware + CAPEX_installation. | (do not fill) |
|  | WACC | % | WACC | This is a fixed value used by the Contracting Authority for economic evaluation. | (do not fill) |
|  | OPEX_yr | €/year | OPEX, per year of preventive maintenance | Total annual cost of preventing maintenance of the BESS including: annual preventive maintenance, remote monitoring, software licences/subscriptions, routine inspections, carried out by the manufacturer or its authorized partners. This should be the fixed yearly cost and cannot be exceeded during the agreed period. |  |
|  | Cycles_yr | cycles/year | Cycles per year | This will be set by the Contracting Authority based on expected operating profile | (do not fill) |
|  | Warranty_cycles | cycles | Cycle count warranty | Total number of full equivalent cycles covered under the battery warranty. This must be the manufacturer‑guaranteed minimum over the system’s life. |  |
|  | EOL_Capacity | % | End of life capacity | Remaining battery capacity at the end of warranty, expressed as a percentage of initial capacity (e.g., 70%, 80%). Must match the warranty document. |  |
|  | DoD | % | DoD window | Recommended Depth of Discharge for normal operation. For example, 90% DoD means 90% of rated capacity can be cycled. |  |
|  | RTE | % | Round trip efficiency (AC/AC) | Measured AC-to-AC round-trip efficiency of the system under typical temperature and load conditions. Should be guaranteed or validated performance. |  |
| 12. | Aux_kWh_yr | kWh/year | Aux. kWh per year | Expected total annual auxiliary energy consumption, including: cooling / HVAC, control systems, BMS/EMS standby load, fire system standby, any other parasitic loads, Should reflect the actual operational profile. |  |
| 13. | Aux_EnergyPrice | €/kWh | Energy price for Aux. | This value is set by the Contracting Authority. | (do not fill) |
| 14. | Aux_Serv | Eur | Cost of auxilary services | Auxiliary services cover all additional operational and technical support activities needed to keep the BESS functioning safely and reliably throughout its lifecycle | (do not fill) |

Annex  to tender

METHODOLOGY FOR CALCULATING THE OVERALL PROPOSAL SCORE

This methodology explains how the contracting authority will evaluate each bid based on the economic performance of the proposed battery energy storage system (BESS). It uses several technical and financial calculations to determine the Levelized Cost of Storage (LCOS) — the final metric used to compare offers.

  - AVERAGE ENERGY CYCLED PER CYCLE IN THE BATTERY SYSTEM,KWH. This calculation determines how much usable energy the battery can discharge during one typical cycle.

EnergyCycled_Avg=CapBESS∙DoD∙1+EOLCapacity2

EnergyCycledAvg-Average energy cycled per cycle in the battery system, kWh

CapBESS- Battery Energy Storage System capacity, kWh

DoD- Depth of Discharge, %.

EOLCapacity- End of Life Capacity, %

  - THE EXPECTED OPERATIONAL DURATION OF THE SYSTEM,YEARS. This calculates how long the system is expected to operate based on the manufacturer’s guaranteed cycles.

Lifetime=CyclesyrWarrantycycles

Lifetime- The expected operational duration of the system, years

Cyclesyr- Number ofchargedischargecycles per year, cycles/year

Warrantycycles- Total number of cycles guaranteed under the manufacturer’s warranty, cycles

  - CAPITAL RECOVERY FACTOR. CRF converts the system’s capital expenditure (Capex) into an annualized cost over the system’s lifetime, taking into account the cost of capital (WACC).

CRF=WACC∙1+WACCLifetime1+WACCLifetime-1

CRF-capital recovery factor

WACC- Weighted Average Cost of Capital, %

Lifetime- The expected operational duration of the system, years

  - YEARLY DISCHARGED ENERGY CAPACITY. This estimates how much energy the system discharges each year, based on cycle energy, number of cycles, and efficiency.

Dischargedyr=EnergyCycledAvg∙Cyclesyr∙RTE

Dischargedyr-Discharged per Year, kWh

EnergyCycledAvg- Energy Cycled Average, kWh

Cyclesyr- Cycles per Year, cycles/year

RTE- Round-Trip Efficiency, %

  - Auxilary services cover all additional operational and technical support activities needed to keep the BESS functioning safely and reliably throughout its lifecycle

Auxserv=CM∙CMh+Auxsyst∙AuxSysste h+TTS∙TTSh+GCT∙GCTh

CM- Corrective Maintenance, eur

CMh- Corrective Maintenance, h

Auxsyst- Auxiliary sytems, Eur

AuxSysste h- Auxiliary sytems, h

TTS- Training & Technical Support, Eur

TTSh- Training & Technical Support, h

GCT- Technical Support During Grid Code Compliance Testing, Eur

GCTh-Technical Support During Grid Code Compliance Testing, h

  - LEVELIZED COST OF STORAGE. The LCOS is a key evaluation metric — it shows how much 1 MWh of stored energy effectively costs over the lifetime of the system.

LCOS=1000∙Capextotal∙CRF+OPEXyr+Auxserv+AuxkWhyr∙AuxEnergyPriceDischargedyr

LCOS- Levelized Cost of Storage, Eur/MWh

Capextotal-Capital Expenditure total, Eur

CRF-capital recovery factor

OPEXyr- Operational Expenditure per Year, Eur/year

AuxkWhyr- Auxiliary Energy in kWh/year

AuxEnergyPrice- Auxiliary Energy Price, Eur

Dischargedyr -Discharged per Year, kWh

Auxserv -Cost of auxiliary services, Eur

If the supplier fails to fill in the information provided in this section, it shall be deemed that there is no confidential information in the supplier's tender.

The control right shall be understood as it is defined in Article 151 of the Law on Public Procurement of the Republic of Lithuania: Controlling person is a legal or natural person who owns another legal person in the following manner:

1) owns over 50 percent of its shares directly or indirectly, or;

2) owns over 50 percent of its shares together with associated persons and owns at least 10 percent of its shares personally. The following shall be considered an associated person:

a) in case of legal persons, persons whose annual financial accountability must be consolidated as per the Law on Consolidated Financial Reporting by Groups of Undertakings of the Republic of Lithuania or the legislation of other countries implementing the requirements set out in the Directive 2013/34/EU.

b) in case of natural persons, spouses, parents and their children (stepchildren).

The right of control is understood as defined in Article (15)1 of the Law on Public Procurement of the Republic of Lithuania: Controlling person – a legal or natural person who, in another legal person:

1) directly or indirectly owns more than 50 percent of shares (parts, shares) or

2) together with related persons owns more than 50 percent of the shares (parts, shares) and whose share is not less than 10 percent of the shares (parts, shares). A related person is considered to be:

a) for the legal entities – persons whose annual financial reporting must be consolidated in accordance with the Law on Consolidated Financial Reporting of Enterprise Groups of the Republic of Lithuania or in accordance with the legal acts of other countries implementing the requirements set forth in Directive 2013/34/EU;

b) for the natural persons – spouses, parents and their children (adopted children).

If the tender for the procurement is signed by a person authorised by the CEO, a written authorisation or another document authorising the right of signing must be appended to the tender.

Sum value from Annex „Tender Price“